## Spatial
Floor | Room | Zone | Row | Rack | Pod | Server | Networking Device | Storage Device
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z1W | ROW-R3-Z1W-R1 | RACK-R3-Z1W-R1-01 | POD-05
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z1W | ROW-R3-Z1W-R1 | RACK-R3-Z1W-R1-02 | POD-05
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z1W | ROW-R3-Z1W-R1 | RACK-R3-Z1W-R1-03 | POD-05
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z1W | ROW-R3-Z1W-R1 | RACK-R3-Z1W-R1-04 | POD-05
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z1W | ROW-R3-Z1W-R1 | RACK-R3-Z1W-R1-05 | POD-05
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z1W | ROW-R3-Z1W-R1 | RACK-R3-Z1W-R1-06 | POD-05
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z1W | ROW-R3-Z1W-R1 | RACK-R3-Z1W-R1-07 | POD-05
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z1W | ROW-R3-Z1W-R1 | RACK-R3-Z1W-R1-08 | POD-05
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z1W | ROW-R3-Z1W-R1 | RACK-R3-Z1W-R1-09 | POD-05
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z1W | ROW-R3-Z1W-R1 | RACK-R3-Z1W-R1-10 | POD-05
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z1W | ROW-R3-Z1W-R1 | RACK-R3-Z1W-R1-11 | POD-05
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z1W | ROW-R3-Z1W-R1 | RACK-R3-Z1W-R1-12 | POD-05
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z1W | ROW-R3-Z1W-R2 | RACK-R3-Z1W-R2-01 | POD-05
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z1W | ROW-R3-Z1W-R2 | RACK-R3-Z1W-R2-02 | POD-05
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z1W | ROW-R3-Z1W-R2 | RACK-R3-Z1W-R2-03 | POD-05
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z1W | ROW-R3-Z1W-R2 | RACK-R3-Z1W-R2-04 | POD-05
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z1W | ROW-R3-Z1W-R2 | RACK-R3-Z1W-R2-05 | POD-05
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z1W | ROW-R3-Z1W-R2 | RACK-R3-Z1W-R2-06 | POD-05
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z1W | ROW-R3-Z1W-R2 | RACK-R3-Z1W-R2-07 | POD-05
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z1W | ROW-R3-Z1W-R2 | RACK-R3-Z1W-R2-08 | POD-05
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z1W | ROW-R3-Z1W-R2 | RACK-R3-Z1W-R2-09 | POD-05
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z1W | ROW-R3-Z1W-R2 | RACK-R3-Z1W-R2-10 | POD-05
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z1W | ROW-R3-Z1W-R2 | RACK-R3-Z1W-R2-11 | POD-05
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z1W | ROW-R3-Z1W-R2 | RACK-R3-Z1W-R2-12 | POD-05
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z2W | ROW-R3-Z2W-R1 | RACK-R3-Z2W-R1-01 | POD-05
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z2W | ROW-R3-Z2W-R1 | RACK-R3-Z2W-R1-02 | POD-05
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z2W | ROW-R3-Z2W-R1 | RACK-R3-Z2W-R1-03 | POD-05
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z2W | ROW-R3-Z2W-R1 | RACK-R3-Z2W-R1-04 | POD-05
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z2W | ROW-R3-Z2W-R1 | RACK-R3-Z2W-R1-05 | POD-05
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z2W | ROW-R3-Z2W-R1 | RACK-R3-Z2W-R1-06 | POD-05
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z2W | ROW-R3-Z2W-R1 | RACK-R3-Z2W-R1-07 | POD-05
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z2W | ROW-R3-Z2W-R1 | RACK-R3-Z2W-R1-08 | POD-05
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z2W | ROW-R3-Z2W-R1 | RACK-R3-Z2W-R1-09 | POD-05
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z2W | ROW-R3-Z2W-R1 | RACK-R3-Z2W-R1-10 | POD-05
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z2W | ROW-R3-Z2W-R1 | RACK-R3-Z2W-R1-11 | POD-05
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z2W | ROW-R3-Z2W-R1 | RACK-R3-Z2W-R1-12 | POD-05
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z2W | ROW-R3-Z2W-R2 | RACK-R3-Z2W-R2-01 | POD-05
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z2W | ROW-R3-Z2W-R2 | RACK-R3-Z2W-R2-02 | POD-05
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z2W | ROW-R3-Z2W-R2 | RACK-R3-Z2W-R2-03 | POD-05
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z2W | ROW-R3-Z2W-R2 | RACK-R3-Z2W-R2-04 | POD-05
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z2W | ROW-R3-Z2W-R2 | RACK-R3-Z2W-R2-05 | POD-05
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z2W | ROW-R3-Z2W-R2 | RACK-R3-Z2W-R2-06 | POD-05
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z2W | ROW-R3-Z2W-R2 | RACK-R3-Z2W-R2-07 | POD-05
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z2W | ROW-R3-Z2W-R2 | RACK-R3-Z2W-R2-08 | POD-05
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z2W | ROW-R3-Z2W-R2 | RACK-R3-Z2W-R2-09 | POD-05
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z2W | ROW-R3-Z2W-R2 | RACK-R3-Z2W-R2-10 | POD-05
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z2W | ROW-R3-Z2W-R2 | RACK-R3-Z2W-R2-11 | POD-05
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z2W | ROW-R3-Z2W-R2 | RACK-R3-Z2W-R2-12 | POD-05
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z3W | ROW-R3-Z3W-R1 | RACK-R3-Z3W-R1-01 | POD-05
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z3W | ROW-R3-Z3W-R1 | RACK-R3-Z3W-R1-02 | POD-05
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z3W | ROW-R3-Z3W-R1 | RACK-R3-Z3W-R1-03 | POD-05
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z3W | ROW-R3-Z3W-R1 | RACK-R3-Z3W-R1-04 | POD-05
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z3W | ROW-R3-Z3W-R1 | RACK-R3-Z3W-R1-05 | POD-05
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z3W | ROW-R3-Z3W-R1 | RACK-R3-Z3W-R1-06 | POD-05
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z3W | ROW-R3-Z3W-R1 | RACK-R3-Z3W-R1-07 | POD-05
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z3W | ROW-R3-Z3W-R1 | RACK-R3-Z3W-R1-08 | POD-05
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z3W | ROW-R3-Z3W-R1 | RACK-R3-Z3W-R1-09 | POD-05
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z3W | ROW-R3-Z3W-R1 | RACK-R3-Z3W-R1-10 | POD-05
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z3W | ROW-R3-Z3W-R1 | RACK-R3-Z3W-R1-11 | POD-05
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z3W | ROW-R3-Z3W-R1 | RACK-R3-Z3W-R1-12 | POD-05
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z3W | ROW-R3-Z3W-R2 | RACK-R3-Z3W-R2-01 | POD-05
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z3W | ROW-R3-Z3W-R2 | RACK-R3-Z3W-R2-02 | POD-05
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z3W | ROW-R3-Z3W-R2 | RACK-R3-Z3W-R2-03 | POD-05
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z3W | ROW-R3-Z3W-R2 | RACK-R3-Z3W-R2-04 | POD-05
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z3W | ROW-R3-Z3W-R2 | RACK-R3-Z3W-R2-05 | POD-05
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z3W | ROW-R3-Z3W-R2 | RACK-R3-Z3W-R2-06 | POD-05
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z3W | ROW-R3-Z3W-R2 | RACK-R3-Z3W-R2-07 | POD-05
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z3W | ROW-R3-Z3W-R2 | RACK-R3-Z3W-R2-08 | POD-05
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z3W | ROW-R3-Z3W-R2 | RACK-R3-Z3W-R2-09 | POD-05
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z3W | ROW-R3-Z3W-R2 | RACK-R3-Z3W-R2-10 | POD-05
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z3W | ROW-R3-Z3W-R2 | RACK-R3-Z3W-R2-11 | POD-05
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z3W | ROW-R3-Z3W-R2 | RACK-R3-Z3W-R2-12 | POD-05
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z4E | ROW-R3-Z4E-R1 | RACK-R3-Z4E-R1-01 | POD-06
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z4E | ROW-R3-Z4E-R1 | RACK-R3-Z4E-R1-02 | POD-06
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z4E | ROW-R3-Z4E-R1 | RACK-R3-Z4E-R1-03 | POD-06
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z4E | ROW-R3-Z4E-R1 | RACK-R3-Z4E-R1-04 | POD-06
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z4E | ROW-R3-Z4E-R1 | RACK-R3-Z4E-R1-05 | POD-06
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z4E | ROW-R3-Z4E-R1 | RACK-R3-Z4E-R1-06 | POD-06
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z4E | ROW-R3-Z4E-R1 | RACK-R3-Z4E-R1-07 | POD-06
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z4E | ROW-R3-Z4E-R1 | RACK-R3-Z4E-R1-08 | POD-06
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z4E | ROW-R3-Z4E-R1 | RACK-R3-Z4E-R1-09 | POD-06
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z4E | ROW-R3-Z4E-R1 | RACK-R3-Z4E-R1-10 | POD-06
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z4E | ROW-R3-Z4E-R1 | RACK-R3-Z4E-R1-11 | POD-06
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z4E | ROW-R3-Z4E-R1 | RACK-R3-Z4E-R1-12 | POD-06
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z4E | ROW-R3-Z4E-R2 | RACK-R3-Z4E-R2-01 | POD-06
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z4E | ROW-R3-Z4E-R2 | RACK-R3-Z4E-R2-02 | POD-06
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z4E | ROW-R3-Z4E-R2 | RACK-R3-Z4E-R2-03 | POD-06
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z4E | ROW-R3-Z4E-R2 | RACK-R3-Z4E-R2-04 | POD-06
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z4E | ROW-R3-Z4E-R2 | RACK-R3-Z4E-R2-05 | POD-06
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z4E | ROW-R3-Z4E-R2 | RACK-R3-Z4E-R2-06 | POD-06
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z4E | ROW-R3-Z4E-R2 | RACK-R3-Z4E-R2-07 | POD-06
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z4E | ROW-R3-Z4E-R2 | RACK-R3-Z4E-R2-08 | POD-06
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z4E | ROW-R3-Z4E-R2 | RACK-R3-Z4E-R2-09 | POD-06
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z4E | ROW-R3-Z4E-R2 | RACK-R3-Z4E-R2-10 | POD-06
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z4E | ROW-R3-Z4E-R2 | RACK-R3-Z4E-R2-11 | POD-06
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z4E | ROW-R3-Z4E-R2 | RACK-R3-Z4E-R2-12 | POD-06
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z5E | ROW-R3-Z5E-R1 | RACK-R3-Z5E-R1-01 | POD-06
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z5E | ROW-R3-Z5E-R1 | RACK-R3-Z5E-R1-02 | POD-06
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z5E | ROW-R3-Z5E-R1 | RACK-R3-Z5E-R1-03 | POD-06
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z5E | ROW-R3-Z5E-R1 | RACK-R3-Z5E-R1-04 | POD-06
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z5E | ROW-R3-Z5E-R1 | RACK-R3-Z5E-R1-05 | POD-06
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z5E | ROW-R3-Z5E-R1 | RACK-R3-Z5E-R1-06 | POD-06
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z5E | ROW-R3-Z5E-R1 | RACK-R3-Z5E-R1-07 | POD-06
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z5E | ROW-R3-Z5E-R1 | RACK-R3-Z5E-R1-08 | POD-06
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z5E | ROW-R3-Z5E-R1 | RACK-R3-Z5E-R1-09 | POD-06
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z5E | ROW-R3-Z5E-R1 | RACK-R3-Z5E-R1-10 | POD-06
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z5E | ROW-R3-Z5E-R1 | RACK-R3-Z5E-R1-11 | POD-06
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z5E | ROW-R3-Z5E-R1 | RACK-R3-Z5E-R1-12 | POD-06
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z5E | ROW-R3-Z5E-R2 | RACK-R3-Z5E-R2-01 | POD-06
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z5E | ROW-R3-Z5E-R2 | RACK-R3-Z5E-R2-02 | POD-06
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z5E | ROW-R3-Z5E-R2 | RACK-R3-Z5E-R2-03 | POD-06
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z5E | ROW-R3-Z5E-R2 | RACK-R3-Z5E-R2-04 | POD-06
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z5E | ROW-R3-Z5E-R2 | RACK-R3-Z5E-R2-05 | POD-06
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z5E | ROW-R3-Z5E-R2 | RACK-R3-Z5E-R2-06 | POD-06
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z5E | ROW-R3-Z5E-R2 | RACK-R3-Z5E-R2-07 | POD-06
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z5E | ROW-R3-Z5E-R2 | RACK-R3-Z5E-R2-08 | POD-06
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z5E | ROW-R3-Z5E-R2 | RACK-R3-Z5E-R2-09 | POD-06
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z5E | ROW-R3-Z5E-R2 | RACK-R3-Z5E-R2-10 | POD-06
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z5E | ROW-R3-Z5E-R2 | RACK-R3-Z5E-R2-11 | POD-06
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z5E | ROW-R3-Z5E-R2 | RACK-R3-Z5E-R2-12 | POD-06
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z6E | ROW-R3-Z6E-R1 | RACK-R3-Z6E-R1-01 | POD-06
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z6E | ROW-R3-Z6E-R1 | RACK-R3-Z6E-R1-02 | POD-06
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z6E | ROW-R3-Z6E-R1 | RACK-R3-Z6E-R1-03 | POD-06
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z6E | ROW-R3-Z6E-R1 | RACK-R3-Z6E-R1-04 | POD-06
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z6E | ROW-R3-Z6E-R1 | RACK-R3-Z6E-R1-05 | POD-06
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z6E | ROW-R3-Z6E-R1 | RACK-R3-Z6E-R1-06 | POD-06
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z6E | ROW-R3-Z6E-R1 | RACK-R3-Z6E-R1-07 | POD-06
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z6E | ROW-R3-Z6E-R1 | RACK-R3-Z6E-R1-08 | POD-06
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z6E | ROW-R3-Z6E-R1 | RACK-R3-Z6E-R1-09 | POD-06
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z6E | ROW-R3-Z6E-R1 | RACK-R3-Z6E-R1-10 | POD-06
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z6E | ROW-R3-Z6E-R1 | RACK-R3-Z6E-R1-11 | POD-06
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z6E | ROW-R3-Z6E-R1 | RACK-R3-Z6E-R1-12 | POD-06
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z6E | ROW-R3-Z6E-R2 | RACK-R3-Z6E-R2-01 | POD-06
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z6E | ROW-R3-Z6E-R2 | RACK-R3-Z6E-R2-02 | POD-06
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z6E | ROW-R3-Z6E-R2 | RACK-R3-Z6E-R2-03 | POD-06
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z6E | ROW-R3-Z6E-R2 | RACK-R3-Z6E-R2-04 | POD-06
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z6E | ROW-R3-Z6E-R2 | RACK-R3-Z6E-R2-05 | POD-06
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z6E | ROW-R3-Z6E-R2 | RACK-R3-Z6E-R2-06 | POD-06
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z6E | ROW-R3-Z6E-R2 | RACK-R3-Z6E-R2-07 | POD-06
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z6E | ROW-R3-Z6E-R2 | RACK-R3-Z6E-R2-08 | POD-06
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z6E | ROW-R3-Z6E-R2 | RACK-R3-Z6E-R2-09 | POD-06
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z6E | ROW-R3-Z6E-R2 | RACK-R3-Z6E-R2-10 | POD-06
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z6E | ROW-R3-Z6E-R2 | RACK-R3-Z6E-R2-11 | POD-06
FLOOR-1 | ROOM-1-3 | ZONE-R3-Z6E | ROW-R3-Z6E-R2 | RACK-R3-Z6E-R2-12 | POD-06
FLOOR-1 | ROOM-1-4 | ZONE-R4-Z1 | ROW-R4-Z1-R1 | RACK-R4-Z1-R1-01 | POD-07
FLOOR-1 | ROOM-1-4 | ZONE-R4-Z1 | ROW-R4-Z1-R1 | RACK-R4-Z1-R1-02 | POD-07
FLOOR-1 | ROOM-1-4 | ZONE-R4-Z1 | ROW-R4-Z1-R1 | RACK-R4-Z1-R1-03 | POD-07
FLOOR-1 | ROOM-1-4 | ZONE-R4-Z1 | ROW-R4-Z1-R1 | RACK-R4-Z1-R1-04 | POD-07
FLOOR-1 | ROOM-1-4 | ZONE-R4-Z1 | ROW-R4-Z1-R1 | RACK-R4-Z1-R1-05 | POD-07
FLOOR-1 | ROOM-1-4 | ZONE-R4-Z1 | ROW-R4-Z1-R1 | RACK-R4-Z1-R1-06 | POD-07
FLOOR-1 | ROOM-1-4 | ZONE-R4-Z1 | ROW-R4-Z1-R1 | RACK-R4-Z1-R1-07 | POD-07
FLOOR-1 | ROOM-1-4 | ZONE-R4-Z1 | ROW-R4-Z1-R1 | RACK-R4-Z1-R1-08 | POD-07
FLOOR-1 | ROOM-1-4 | ZONE-R4-Z1 | ROW-R4-Z1-R1 | RACK-R4-Z1-R1-09 | POD-07
FLOOR-1 | ROOM-1-4 | ZONE-R4-Z1 | ROW-R4-Z1-R1 | RACK-R4-Z1-R1-10 | POD-07
FLOOR-1 | ROOM-1-4 | ZONE-R4-Z1 | ROW-R4-Z1-R1 | RACK-R4-Z1-R1-11 | POD-07
FLOOR-1 | ROOM-1-4 | ZONE-R4-Z1 | ROW-R4-Z1-R1 | RACK-R4-Z1-R1-12 | POD-07
FLOOR-1 | ROOM-1-4 | ZONE-R4-Z1 | ROW-R4-Z1-R2 | RACK-R4-Z1-R2-01 | POD-07
FLOOR-1 | ROOM-1-4 | ZONE-R4-Z1 | ROW-R4-Z1-R2 | RACK-R4-Z1-R2-02 | POD-07
FLOOR-1 | ROOM-1-4 | ZONE-R4-Z1 | ROW-R4-Z1-R2 | RACK-R4-Z1-R2-03 | POD-07
FLOOR-1 | ROOM-1-4 | ZONE-R4-Z1 | ROW-R4-Z1-R2 | RACK-R4-Z1-R2-04 | POD-07
FLOOR-1 | ROOM-1-4 | ZONE-R4-Z1 | ROW-R4-Z1-R2 | RACK-R4-Z1-R2-05 | POD-07
FLOOR-1 | ROOM-1-4 | ZONE-R4-Z1 | ROW-R4-Z1-R2 | RACK-R4-Z1-R2-06 | POD-07
FLOOR-1 | ROOM-1-4 | ZONE-R4-Z1 | ROW-R4-Z1-R2 | RACK-R4-Z1-R2-07 | POD-07
FLOOR-1 | ROOM-1-4 | ZONE-R4-Z1 | ROW-R4-Z1-R2 | RACK-R4-Z1-R2-08 | POD-07
FLOOR-1 | ROOM-1-4 | ZONE-R4-Z1 | ROW-R4-Z1-R2 | RACK-R4-Z1-R2-09 | POD-07
FLOOR-1 | ROOM-1-4 | ZONE-R4-Z1 | ROW-R4-Z1-R2 | RACK-R4-Z1-R2-10 | POD-07
FLOOR-1 | ROOM-1-4 | ZONE-R4-Z1 | ROW-R4-Z1-R2 | RACK-R4-Z1-R2-11 | POD-07
FLOOR-1 | ROOM-1-4 | ZONE-R4-Z1 | ROW-R4-Z1-R2 | RACK-R4-Z1-R2-12 | POD-07
FLOOR-1 | ROOM-1-5 | ZONE-R5-Z1W | ROW-R5-Z1W-R1 | RACK-R5-Z1W-R1-01 | POD-08
FLOOR-1 | ROOM-1-5 | ZONE-R5-Z1W | ROW-R5-Z1W-R1 | RACK-R5-Z1W-R1-02 | POD-08
FLOOR-1 | ROOM-1-5 | ZONE-R5-Z1W | ROW-R5-Z1W-R1 | RACK-R5-Z1W-R1-03 | POD-08
FLOOR-1 | ROOM-1-5 | ZONE-R5-Z1W | ROW-R5-Z1W-R1 | RACK-R5-Z1W-R1-04 | POD-08
FLOOR-1 | ROOM-1-5 | ZONE-R5-Z1W | ROW-R5-Z1W-R1 | RACK-R5-Z1W-R1-05 | POD-08
FLOOR-1 | ROOM-1-5 | ZONE-R5-Z1W | ROW-R5-Z1W-R1 | RACK-R5-Z1W-R1-06 | POD-08
FLOOR-1 | ROOM-1-5 | ZONE-R5-Z1W | ROW-R5-Z1W-R1 | RACK-R5-Z1W-R1-07 | POD-08
FLOOR-1 | ROOM-1-5 | ZONE-R5-Z1W | ROW-R5-Z1W-R1 | RACK-R5-Z1W-R1-08 | POD-08
FLOOR-1 | ROOM-1-5 | ZONE-R5-Z1W | ROW-R5-Z1W-R1 | RACK-R5-Z1W-R1-09 | POD-08
FLOOR-1 | ROOM-1-5 | ZONE-R5-Z1W | ROW-R5-Z1W-R1 | RACK-R5-Z1W-R1-10 | POD-08
FLOOR-1 | ROOM-1-5 | ZONE-R5-Z1W | ROW-R5-Z1W-R1 | RACK-R5-Z1W-R1-11 | POD-08
FLOOR-1 | ROOM-1-5 | ZONE-R5-Z1W | ROW-R5-Z1W-R1 | RACK-R5-Z1W-R1-12 | POD-08
FLOOR-1 | ROOM-1-5 | ZONE-R5-Z1W | ROW-R5-Z1W-R2 | RACK-R5-Z1W-R2-01 | POD-08
FLOOR-1 | ROOM-1-5 | ZONE-R5-Z1W | ROW-R5-Z1W-R2 | RACK-R5-Z1W-R2-02 | POD-08
FLOOR-1 | ROOM-1-5 | ZONE-R5-Z1W | ROW-R5-Z1W-R2 | RACK-R5-Z1W-R2-03 | POD-08
FLOOR-1 | ROOM-1-5 | ZONE-R5-Z1W | ROW-R5-Z1W-R2 | RACK-R5-Z1W-R2-04 | POD-08
FLOOR-1 | ROOM-1-5 | ZONE-R5-Z1W | ROW-R5-Z1W-R2 | RACK-R5-Z1W-R2-05 | POD-08
FLOOR-1 | ROOM-1-5 | ZONE-R5-Z1W | ROW-R5-Z1W-R2 | RACK-R5-Z1W-R2-06 | POD-08
FLOOR-1 | ROOM-1-5 | ZONE-R5-Z1W | ROW-R5-Z1W-R2 | RACK-R5-Z1W-R2-07 | POD-08
FLOOR-1 | ROOM-1-5 | ZONE-R5-Z1W | ROW-R5-Z1W-R2 | RACK-R5-Z1W-R2-08 | POD-08
FLOOR-1 | ROOM-1-5 | ZONE-R5-Z1W | ROW-R5-Z1W-R2 | RACK-R5-Z1W-R2-09 | POD-08
FLOOR-1 | ROOM-1-5 | ZONE-R5-Z1W | ROW-R5-Z1W-R2 | RACK-R5-Z1W-R2-10 | POD-08
FLOOR-1 | ROOM-1-5 | ZONE-R5-Z1W | ROW-R5-Z1W-R2 | RACK-R5-Z1W-R2-11 | POD-08
FLOOR-1 | ROOM-1-5 | ZONE-R5-Z1W | ROW-R5-Z1W-R2 | RACK-R5-Z1W-R2-12 | POD-08
FLOOR-1 | ROOM-1-5 | ZONE-R5-Z2E | ROW-R5-Z2E-R1 | RACK-R5-Z2E-R1-01 | POD-09
FLOOR-1 | ROOM-1-5 | ZONE-R5-Z2E | ROW-R5-Z2E-R1 | RACK-R5-Z2E-R1-02 | POD-09
FLOOR-1 | ROOM-1-5 | ZONE-R5-Z2E | ROW-R5-Z2E-R1 | RACK-R5-Z2E-R1-03 | POD-09
FLOOR-1 | ROOM-1-5 | ZONE-R5-Z2E | ROW-R5-Z2E-R1 | RACK-R5-Z2E-R1-04 | POD-09
FLOOR-1 | ROOM-1-5 | ZONE-R5-Z2E | ROW-R5-Z2E-R1 | RACK-R5-Z2E-R1-05 | POD-09
FLOOR-1 | ROOM-1-5 | ZONE-R5-Z2E | ROW-R5-Z2E-R1 | RACK-R5-Z2E-R1-06 | POD-09
FLOOR-1 | ROOM-1-5 | ZONE-R5-Z2E | ROW-R5-Z2E-R1 | RACK-R5-Z2E-R1-07 | POD-09
FLOOR-1 | ROOM-1-5 | ZONE-R5-Z2E | ROW-R5-Z2E-R1 | RACK-R5-Z2E-R1-08 | POD-09
FLOOR-1 | ROOM-1-5 | ZONE-R5-Z2E | ROW-R5-Z2E-R1 | RACK-R5-Z2E-R1-09 | POD-09
FLOOR-1 | ROOM-1-5 | ZONE-R5-Z2E | ROW-R5-Z2E-R1 | RACK-R5-Z2E-R1-10 | POD-09
FLOOR-1 | ROOM-1-5 | ZONE-R5-Z2E | ROW-R5-Z2E-R1 | RACK-R5-Z2E-R1-11 | POD-09
FLOOR-1 | ROOM-1-5 | ZONE-R5-Z2E | ROW-R5-Z2E-R1 | RACK-R5-Z2E-R1-12 | POD-09
FLOOR-1 | ROOM-1-5 | ZONE-R5-Z2E | ROW-R5-Z2E-R2 | RACK-R5-Z2E-R2-01 | POD-09
FLOOR-1 | ROOM-1-5 | ZONE-R5-Z2E | ROW-R5-Z2E-R2 | RACK-R5-Z2E-R2-02 | POD-09
FLOOR-1 | ROOM-1-5 | ZONE-R5-Z2E | ROW-R5-Z2E-R2 | RACK-R5-Z2E-R2-03 | POD-09
FLOOR-1 | ROOM-1-5 | ZONE-R5-Z2E | ROW-R5-Z2E-R2 | RACK-R5-Z2E-R2-04 | POD-09
FLOOR-1 | ROOM-1-5 | ZONE-R5-Z2E | ROW-R5-Z2E-R2 | RACK-R5-Z2E-R2-05 | POD-09
FLOOR-1 | ROOM-1-5 | ZONE-R5-Z2E | ROW-R5-Z2E-R2 | RACK-R5-Z2E-R2-06 | POD-09
FLOOR-1 | ROOM-1-5 | ZONE-R5-Z2E | ROW-R5-Z2E-R2 | RACK-R5-Z2E-R2-07 | POD-09
FLOOR-1 | ROOM-1-5 | ZONE-R5-Z2E | ROW-R5-Z2E-R2 | RACK-R5-Z2E-R2-08 | POD-09
FLOOR-1 | ROOM-1-5 | ZONE-R5-Z2E | ROW-R5-Z2E-R2 | RACK-R5-Z2E-R2-09 | POD-09
FLOOR-1 | ROOM-1-5 | ZONE-R5-Z2E | ROW-R5-Z2E-R2 | RACK-R5-Z2E-R2-10 | POD-09
FLOOR-1 | ROOM-1-5 | ZONE-R5-Z2E | ROW-R5-Z2E-R2 | RACK-R5-Z2E-R2-11 | POD-09
FLOOR-1 | ROOM-1-5 | ZONE-R5-Z2E | ROW-R5-Z2E-R2 | RACK-R5-Z2E-R2-12 | POD-09

## Zone-Aisle
Zone | Aisle
ZONE-R3-Z1W | AISLE-R3-Z1W-R1H
ZONE-R3-Z1W | AISLE-R3-Z1W-R1R2C
ZONE-R3-Z2W | AISLE-R3-Z2W-R1H
ZONE-R3-Z2W | AISLE-R3-Z2W-R1R2C
ZONE-R3-Z3W | AISLE-R3-Z3W-R1H
ZONE-R3-Z3W | AISLE-R3-Z3W-R1R2C
ZONE-R3-Z3W | AISLE-R3-Z3W-R2H
ZONE-R3-Z4E | AISLE-R3-Z4E-R1H
ZONE-R3-Z4E | AISLE-R3-Z4E-R1R2C
ZONE-R3-Z5E | AISLE-R3-Z5E-R1H
ZONE-R3-Z5E | AISLE-R3-Z5E-R1R2C
ZONE-R3-Z6E | AISLE-R3-Z6E-R1H
ZONE-R3-Z6E | AISLE-R3-Z6E-R1R2C
ZONE-R3-Z6E | AISLE-R3-Z6E-R2H
ZONE-R4-Z1 | AISLE-R4-Z1-R1H
ZONE-R4-Z1 | AISLE-R4-Z1-R1R2C
ZONE-R4-Z1 | AISLE-R4-Z1-R2H
ZONE-R5-Z1W | AISLE-R5-Z1W-R1H
ZONE-R5-Z1W | AISLE-R5-Z1W-R1R2C
ZONE-R5-Z1W | AISLE-R5-Z1W-R2H
ZONE-R5-Z2E | AISLE-R5-Z2E-R1H
ZONE-R5-Z2E | AISLE-R5-Z2E-R1R2C
ZONE-R5-Z2E | AISLE-R5-Z2E-R2H

## Sheet2
Count of Rack
Capacity Cell | Total
CC-R1R2 | 48
CC-R3 | 144
CC-R4 | 24
CC-R5E | 24
CC-R5W | 24
(blank)
Grand Total | 264

## Master_Rack
Zone | Row | Planned Rack Density (kW) | Cold Aisle | Hot Aisle | Liquid Loop | Air Zone | Rack | Pod | Rack PDU (A Feed) | Rack PDU (B Feed) | Rack_Circuit_Capacity_(design) | Rack_Max_Liquid_Load | Rack_Max_Air_Load | Rack_Circuit_Capacity_(rated) | Rack_LiquidCool_Fraction | Rack_AirCool_Fraction | RPP (A Feed) | RPP (B Feed) | Room PDU (A Feed) | Room PDU (B Feed) | UPS (A Feed) | UPS (B Feed) | BESS | Switch Gear (A Feed) | Switch Gear (B Feed) | Utility (A Feed) | Utility (B Feed) | Generator (A Feed) | Generator (B Feed) | Capacity Cell | Room Bundle | Room PDU Bundle | UPS Bundle | ITL-SJ-Meridian-C01-PP01 | LCL-SJ-Meridian-C01-PP01 | ACL-SJ-Meridian-C01-PP01 | ITL-SJ-Pacific-C01-PD01 | LCL-SJ-Pacific-C01-PD01 | ACL-SJ-Pacific-C01-PD01 | ITL-SJ-Pacific-C01-PD02 | ACL-SJ-Pacific-C01-PD02 | LCL-SJ-Pacific-C01-PD02 | ITL-SJ-Pacific-C01-PD03 | ACL-SJ-Pacific-C01-PD03 | LCL-SJ-Pacific-C01-PD03 | ITL-SJ-Pacific-C01-PD04 | ACL-SJ-Pacific-C01-PD04 | LCL-SJ-Pacific-C01-PD04 | ITL-SJ-Keystone-C01-PP01 | ACL-SJ-Keystone-C01-PP01 | LCL-SJ-Keystone-C01-PP01 | LCM-SJ-Meridian-C01-PP01 | LCM-SJ-Pacific-C01-PD01 | LCM-SJ-Pacific-C01-PD02 | LCM-SJ-Pacific-C01-PD03 | LCM-SJ-Pacific-C01-PD04 | LCM-SJ-Keystone-C01-PP01 | LCM-SJ-Meridian-C01-PP01% | LCM-SJ-Pacific-C01-PD01% | LCM-SJ-Pacific-C01-PD02% | LCM-SJ-Pacific-C01-PD03% | LCM-SJ-Pacific-C01-PD04% | LCM-SJ-Keystone-C01-PP01% | RDHx | RDHx_MaxHeat_Removal | DTC | DTC_MaxCool_Capacity | COUNT-SJ-Meridian-C01-PP01 | COUNT-SJ-Pacific-C01-PD01 | COUNT-SJ-Pacific-C01-PD02 | COUNT-SJ-Pacific-C01-PD03 | COUNT-SJ-Pacific-C01-PD04 | COUNT-SJ-Keystone-C01-PP01
ZONE-R3-Z1W | ROW-R3-Z1W-R1 | 30 |  |  | LL-R3-W | AIRZONE-R3-W1 | RACK-R3-Z1W-R1-01 | POD-05 | RACKPDU-RACK-R3-Z1W-R1-01-A | RACKPDU-RACK-R3-Z1W-R1-01-B | 30 | 22.5 | 7.5 | 36 | 75% | 25% | RPP-R3-A1 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 30 | 22.5 | 7.5 | 30 | 22.5 | 7.5 | [9 empty] | 30 | 0 | 0 | 30 | 30 | 30 | 100% | 0% | 0% | 100% | 100% | 100% |  |  | DTC-RACK-R3-Z1W-R1-01 | 25 | 0 | 1 | 1 | 0 | 0 | 0
ZONE-R3-Z1W | ROW-R3-Z1W-R1 | 30 |  |  | LL-R3-W | AIRZONE-R3-W1 | RACK-R3-Z1W-R1-02 | POD-05 | RACKPDU-RACK-R3-Z1W-R1-02-A | RACKPDU-RACK-R3-Z1W-R1-02-B | 30 | 22.5 | 7.5 | 36 | 75% | 25% | RPP-R3-A1 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 30 | 22.5 | 7.5 | 30 | 22.5 | 7.5 | [9 empty] | 30 | 0 | 0 | 30 | 30 | 30 | 100% | 0% | 0% | 100% | 100% | 100% |  |  | DTC-RACK-R3-Z1W-R1-02 | 25 | 0 | 1 | 1 | 0 | 0 | 0
ZONE-R3-Z1W | ROW-R3-Z1W-R1 | 30 |  |  | LL-R3-W | AIRZONE-R3-W1 | RACK-R3-Z1W-R1-03 | POD-05 | RACKPDU-RACK-R3-Z1W-R1-03-A | RACKPDU-RACK-R3-Z1W-R1-03-B | 30 | 22.5 | 7.5 | 36 | 75% | 25% | RPP-R3-A1 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 30 | 22.5 | 7.5 | 30 | 22.5 | 7.5 | [9 empty] | 30 | 0 | 0 | 30 | 30 | 30 | 100% | 0% | 0% | 100% | 100% | 100% |  |  | DTC-RACK-R3-Z1W-R1-03 | 25 | 0 | 1 | 1 | 0 | 0 | 0
ZONE-R3-Z1W | ROW-R3-Z1W-R1 | 30 |  |  | LL-R3-W | AIRZONE-R3-W1 | RACK-R3-Z1W-R1-04 | POD-05 | RACKPDU-RACK-R3-Z1W-R1-04-A | RACKPDU-RACK-R3-Z1W-R1-04-B | 30 | 22.5 | 7.5 | 36 | 75% | 25% | RPP-R3-A1 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 30 | 22.5 | 7.5 | 30 | 22.5 | 7.5 | [9 empty] | 30 | 0 | 0 | 30 | 30 | 30 | 100% | 0% | 0% | 100% | 100% | 100% |  |  | DTC-RACK-R3-Z1W-R1-04 | 25 | 0 | 1 | 1 | 0 | 0 | 0
ZONE-R3-Z1W | ROW-R3-Z1W-R1 | 30 |  |  | LL-R3-W | AIRZONE-R3-W1 | RACK-R3-Z1W-R1-05 | POD-05 | RACKPDU-RACK-R3-Z1W-R1-05-A | RACKPDU-RACK-R3-Z1W-R1-05-B | 30 | 22.5 | 7.5 | 36 | 75% | 25% | RPP-R3-A2 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 30 | 22.5 | 7.5 | 30 | 22.5 | 7.5 | [9 empty] | 30 | 0 | 0 | 30 | 30 | 30 | 100% | 0% | 0% | 100% | 100% | 100% |  |  | DTC-RACK-R3-Z1W-R1-05 | 25 | 0 | 1 | 1 | 0 | 0 | 0
ZONE-R3-Z1W | ROW-R3-Z1W-R1 | 30 |  |  | LL-R3-W | AIRZONE-R3-W1 | RACK-R3-Z1W-R1-06 | POD-05 | RACKPDU-RACK-R3-Z1W-R1-06-A | RACKPDU-RACK-R3-Z1W-R1-06-B | 30 | 22.5 | 7.5 | 36 | 75% | 25% | RPP-R3-A2 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 30 | 22.5 | 7.5 | 30 | 22.5 | 7.5 | [9 empty] | 30 | 0 | 0 | 30 | 30 | 30 | 100% | 0% | 0% | 100% | 100% | 100% |  |  | DTC-RACK-R3-Z1W-R1-06 | 25 | 0 | 1 | 1 | 0 | 0 | 0
ZONE-R3-Z1W | ROW-R3-Z1W-R1 | 30 |  |  | LL-R3-W | AIRZONE-R3-W1 | RACK-R3-Z1W-R1-07 | POD-05 | RACKPDU-RACK-R3-Z1W-R1-07-A | RACKPDU-RACK-R3-Z1W-R1-07-B | 30 | 22.5 | 7.5 | 36 | 75% | 25% | RPP-R3-A2 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 30 | 22.5 | 7.5 | 30 | 22.5 | 7.5 | [9 empty] | 30 | 0 | 0 | 30 | 30 | 30 | 100% | 0% | 0% | 100% | 100% | 100% |  |  | DTC-RACK-R3-Z1W-R1-07 | 25 | 0 | 1 | 1 | 0 | 0 | 0
ZONE-R3-Z1W | ROW-R3-Z1W-R1 | 30 |  |  | LL-R3-W | AIRZONE-R3-W1 | RACK-R3-Z1W-R1-08 | POD-05 | RACKPDU-RACK-R3-Z1W-R1-08-A | RACKPDU-RACK-R3-Z1W-R1-08-B | 30 | 22.5 | 7.5 | 36 | 75% | 25% | RPP-R3-A2 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 30 | 22.5 | 7.5 | 30 | 22.5 | 7.5 | [9 empty] | 30 | 0 | 0 | 30 | 30 | 30 | 100% | 0% | 0% | 100% | 100% | 100% |  |  | DTC-RACK-R3-Z1W-R1-08 | 25 | 0 | 1 | 1 | 0 | 0 | 0
ZONE-R3-Z1W | ROW-R3-Z1W-R1 | 30 |  |  | LL-R3-W | AIRZONE-R3-W1 | RACK-R3-Z1W-R1-09 | POD-05 | RACKPDU-RACK-R3-Z1W-R1-09-A | RACKPDU-RACK-R3-Z1W-R1-09-B | 30 | 22.5 | 7.5 | 36 | 75% | 25% | RPP-R3-A1 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 30 | 22.5 | 7.5 | 0 | 0 | 0 | [9 empty] | 30 | 0 | 30 | 30 | 30 | 30 | 100% | 0% | 100% | 100% | 100% | 100% |  |  | DTC-RACK-R3-Z1W-R1-09 | 25 | 0 | 1 | 0 | 0 | 0 | 0
ZONE-R3-Z1W | ROW-R3-Z1W-R1 | 30 |  |  | LL-R3-W | AIRZONE-R3-W1 | RACK-R3-Z1W-R1-10 | POD-05 | RACKPDU-RACK-R3-Z1W-R1-10-A | RACKPDU-RACK-R3-Z1W-R1-10-B | 30 | 22.5 | 7.5 | 36 | 75% | 25% | RPP-R3-A1 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 30 | 22.5 | 7.5 | 0 | 0 | 0 | [9 empty] | 30 | 0 | 30 | 30 | 30 | 30 | 100% | 0% | 100% | 100% | 100% | 100% |  |  | DTC-RACK-R3-Z1W-R1-10 | 25 | 0 | 1 | 0 | 0 | 0 | 0
ZONE-R3-Z1W | ROW-R3-Z1W-R1 | 30 |  |  | LL-R3-W | AIRZONE-R3-W1 | RACK-R3-Z1W-R1-11 | POD-05 | RACKPDU-RACK-R3-Z1W-R1-11-A | RACKPDU-RACK-R3-Z1W-R1-11-B | 30 | 22.5 | 7.5 | 36 | 75% | 25% | RPP-R3-A1 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 30 | 22.5 | 7.5 | 0 | 0 | 0 | [9 empty] | 30 | 0 | 30 | 30 | 30 | 30 | 100% | 0% | 100% | 100% | 100% | 100% |  |  | DTC-RACK-R3-Z1W-R1-11 | 25 | 0 | 1 | 0 | 0 | 0 | 0
ZONE-R3-Z1W | ROW-R3-Z1W-R1 | 30 |  |  | LL-R3-W | AIRZONE-R3-W1 | RACK-R3-Z1W-R1-12 | POD-05 | RACKPDU-RACK-R3-Z1W-R1-12-A | RACKPDU-RACK-R3-Z1W-R1-12-B | 30 | 22.5 | 7.5 | 36 | 75% | 25% | RPP-R3-A1 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 30 | 22.5 | 7.5 | 0 | 0 | 0 | [9 empty] | 30 | 0 | 30 | 30 | 30 | 30 | 100% | 0% | 100% | 100% | 100% | 100% |  |  | DTC-RACK-R3-Z1W-R1-12 | 25 | 0 | 1 | 0 | 0 | 0 | 0
ZONE-R3-Z1W | ROW-R3-Z1W-R2 | 30 |  |  | LL-R3-W | AIRZONE-R3-W1 | RACK-R3-Z1W-R2-01 | POD-05 | RACKPDU-RACK-R3-Z1W-R2-01-A | RACKPDU-RACK-R3-Z1W-R2-01-B | 30 | 22.5 | 7.5 | 36 | 75% | 25% | RPP-R3-A2 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 30 | 22.5 | 7.5 | [9 empty] | 30 | 30 | 0 | 30 | 30 | 30 | 100% | 100% | 0% | 100% | 100% | 100% |  |  | DTC-RACK-R3-Z1W-R2-01 | 25 | 0 | 0 | 1 | 0 | 0 | 0
ZONE-R3-Z1W | ROW-R3-Z1W-R2 | 30 |  |  | LL-R3-W | AIRZONE-R3-W1 | RACK-R3-Z1W-R2-02 | POD-05 | RACKPDU-RACK-R3-Z1W-R2-02-A | RACKPDU-RACK-R3-Z1W-R2-02-B | 30 | 22.5 | 7.5 | 36 | 75% | 25% | RPP-R3-A2 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 30 | 22.5 | 7.5 | [9 empty] | 30 | 30 | 0 | 30 | 30 | 30 | 100% | 100% | 0% | 100% | 100% | 100% |  |  | DTC-RACK-R3-Z1W-R2-02 | 25 | 0 | 0 | 1 | 0 | 0 | 0
ZONE-R3-Z1W | ROW-R3-Z1W-R2 | 30 |  |  | LL-R3-W | AIRZONE-R3-W1 | RACK-R3-Z1W-R2-03 | POD-05 | RACKPDU-RACK-R3-Z1W-R2-03-A | RACKPDU-RACK-R3-Z1W-R2-03-B | 30 | 22.5 | 7.5 | 36 | 75% | 25% | RPP-R3-A2 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 30 | 22.5 | 7.5 | [9 empty] | 30 | 30 | 0 | 30 | 30 | 30 | 100% | 100% | 0% | 100% | 100% | 100% |  |  | DTC-RACK-R3-Z1W-R2-03 | 25 | 0 | 0 | 1 | 0 | 0 | 0
ZONE-R3-Z1W | ROW-R3-Z1W-R2 | 30 |  |  | LL-R3-W | AIRZONE-R3-W1 | RACK-R3-Z1W-R2-04 | POD-05 | RACKPDU-RACK-R3-Z1W-R2-04-A | RACKPDU-RACK-R3-Z1W-R2-04-B | 30 | 22.5 | 7.5 | 36 | 75% | 25% | RPP-R3-A2 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 30 | 22.5 | 7.5 | [9 empty] | 30 | 30 | 0 | 30 | 30 | 30 | 100% | 100% | 0% | 100% | 100% | 100% |  |  | DTC-RACK-R3-Z1W-R2-04 | 25 | 0 | 0 | 1 | 0 | 0 | 0
ZONE-R3-Z1W | ROW-R3-Z1W-R2 | 30 |  |  | LL-R3-W | AIRZONE-R3-W1 | RACK-R3-Z1W-R2-05 | POD-05 | RACKPDU-RACK-R3-Z1W-R2-05-A | RACKPDU-RACK-R3-Z1W-R2-05-B | 30 | 22.5 | 7.5 | 36 | 75% | 25% | RPP-R3-A1 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 30 | 22.5 | 7.5 | 30 | 22.5 | 7.5 | [9 empty] | 30 | 0 | 0 | 30 | 30 | 30 | 100% | 0% | 0% | 100% | 100% | 100% |  |  | DTC-RACK-R3-Z1W-R2-05 | 25 | 0 | 1 | 1 | 0 | 0 | 0
ZONE-R3-Z1W | ROW-R3-Z1W-R2 | 30 |  |  | LL-R3-W | AIRZONE-R3-W1 | RACK-R3-Z1W-R2-06 | POD-05 | RACKPDU-RACK-R3-Z1W-R2-06-A | RACKPDU-RACK-R3-Z1W-R2-06-B | 30 | 22.5 | 7.5 | 36 | 75% | 25% | RPP-R3-A1 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 30 | 22.5 | 7.5 | 30 | 22.5 | 7.5 | [9 empty] | 30 | 0 | 0 | 30 | 30 | 30 | 100% | 0% | 0% | 100% | 100% | 100% |  |  | DTC-RACK-R3-Z1W-R2-06 | 25 | 0 | 1 | 1 | 0 | 0 | 0
ZONE-R3-Z1W | ROW-R3-Z1W-R2 | 30 |  |  | LL-R3-W | AIRZONE-R3-W1 | RACK-R3-Z1W-R2-07 | POD-05 | RACKPDU-RACK-R3-Z1W-R2-07-A | RACKPDU-RACK-R3-Z1W-R2-07-B | 30 | 22.5 | 7.5 | 36 | 75% | 25% | RPP-R3-A1 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 30 | 22.5 | 7.5 | 0 | 0 | 0 | [9 empty] | 30 | 0 | 30 | 30 | 30 | 30 | 100% | 0% | 100% | 100% | 100% | 100% |  |  | DTC-RACK-R3-Z1W-R2-07 | 25 | 0 | 1 | 0 | 0 | 0 | 0
ZONE-R3-Z1W | ROW-R3-Z1W-R2 | 30 |  |  | LL-R3-W | AIRZONE-R3-W1 | RACK-R3-Z1W-R2-08 | POD-05 | RACKPDU-RACK-R3-Z1W-R2-08-A | RACKPDU-RACK-R3-Z1W-R2-08-B | 30 | 22.5 | 7.5 | 36 | 75% | 25% | RPP-R3-A1 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 30 | 22.5 | 7.5 | 0 | 0 | 0 | [9 empty] | 30 | 0 | 30 | 30 | 30 | 30 | 100% | 0% | 100% | 100% | 100% | 100% |  |  | DTC-RACK-R3-Z1W-R2-08 | 25 | 0 | 1 | 0 | 0 | 0 | 0
ZONE-R3-Z1W | ROW-R3-Z1W-R2 | 30 |  |  | LL-R3-W | AIRZONE-R3-W1 | RACK-R3-Z1W-R2-09 | POD-05 | RACKPDU-RACK-R3-Z1W-R2-09-A | RACKPDU-RACK-R3-Z1W-R2-09-B | 30 | 22.5 | 7.5 | 36 | 75% | 25% | RPP-R3-A2 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 30 | 22.5 | 7.5 | [9 empty] | 30 | 30 | 0 | 30 | 30 | 30 | 100% | 100% | 0% | 100% | 100% | 100% |  |  | DTC-RACK-R3-Z1W-R2-09 | 25 | 0 | 0 | 1 | 0 | 0 | 0
ZONE-R3-Z1W | ROW-R3-Z1W-R2 | 30 |  |  | LL-R3-W | AIRZONE-R3-W1 | RACK-R3-Z1W-R2-10 | POD-05 | RACKPDU-RACK-R3-Z1W-R2-10-A | RACKPDU-RACK-R3-Z1W-R2-10-B | 30 | 22.5 | 7.5 | 36 | 75% | 25% | RPP-R3-A2 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 30 | 22.5 | 7.5 | [9 empty] | 30 | 30 | 0 | 30 | 30 | 30 | 100% | 100% | 0% | 100% | 100% | 100% |  |  | DTC-RACK-R3-Z1W-R2-10 | 25 | 0 | 0 | 1 | 0 | 0 | 0
ZONE-R3-Z1W | ROW-R3-Z1W-R2 | 30 |  |  | LL-R3-W | AIRZONE-R3-W1 | RACK-R3-Z1W-R2-11 | POD-05 | RACKPDU-RACK-R3-Z1W-R2-11-A | RACKPDU-RACK-R3-Z1W-R2-11-B | 30 | 22.5 | 7.5 | 36 | 75% | 25% | RPP-R3-A2 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 30 | 22.5 | 7.5 | [9 empty] | 30 | 30 | 0 | 30 | 30 | 30 | 100% | 100% | 0% | 100% | 100% | 100% |  |  | DTC-RACK-R3-Z1W-R2-11 | 25 | 0 | 0 | 1 | 0 | 0 | 0
ZONE-R3-Z1W | ROW-R3-Z1W-R2 | 30 |  |  | LL-R3-W | AIRZONE-R3-W1 | RACK-R3-Z1W-R2-12 | POD-05 | RACKPDU-RACK-R3-Z1W-R2-12-A | RACKPDU-RACK-R3-Z1W-R2-12-B | 30 | 22.5 | 7.5 | 36 | 75% | 25% | RPP-R3-A2 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 30 | 22.5 | 7.5 | [9 empty] | 30 | 30 | 0 | 30 | 30 | 30 | 100% | 100% | 0% | 100% | 100% | 100% |  |  | DTC-RACK-R3-Z1W-R2-12 | 25 | 0 | 0 | 1 | 0 | 0 | 0
ZONE-R3-Z2W | ROW-R3-Z2W-R1 | 30 |  |  | LL-R3-W | AIRZONE-R3-W1 | RACK-R3-Z2W-R1-01 | POD-05 | RACKPDU-RACK-R3-Z2W-R1-01-A | RACKPDU-RACK-R3-Z2W-R1-01-B | 30 | 22.5 | 7.5 | 36 | 75% | 25% | RPP-R3-A1 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 30 | 22.5 | 7.5 | 0 | 0 | 0 | [9 empty] | 30 | 0 | 30 | 30 | 30 | 30 | 100% | 0% | 100% | 100% | 100% | 100% |  |  | DTC-RACK-R3-Z2W-R1-01 | 25 | 0 | 1 | 0 | 0 | 0 | 0
ZONE-R3-Z2W | ROW-R3-Z2W-R1 | 30 |  |  | LL-R3-W | AIRZONE-R3-W1 | RACK-R3-Z2W-R1-02 | POD-05 | RACKPDU-RACK-R3-Z2W-R1-02-A | RACKPDU-RACK-R3-Z2W-R1-02-B | 30 | 22.5 | 7.5 | 36 | 75% | 25% | RPP-R3-A1 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 30 | 22.5 | 7.5 | 0 | 0 | 0 | [9 empty] | 30 | 0 | 30 | 30 | 30 | 30 | 100% | 0% | 100% | 100% | 100% | 100% |  |  | DTC-RACK-R3-Z2W-R1-02 | 25 | 0 | 1 | 0 | 0 | 0 | 0
ZONE-R3-Z2W | ROW-R3-Z2W-R1 | 30 |  |  | LL-R3-W | AIRZONE-R3-W1 | RACK-R3-Z2W-R1-03 | POD-05 | RACKPDU-RACK-R3-Z2W-R1-03-A | RACKPDU-RACK-R3-Z2W-R1-03-B | 30 | 22.5 | 7.5 | 36 | 75% | 25% | RPP-R3-A1 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 30 | 22.5 | 7.5 | 0 | 0 | 0 | [9 empty] | 30 | 0 | 30 | 30 | 30 | 30 | 100% | 0% | 100% | 100% | 100% | 100% |  |  | DTC-RACK-R3-Z2W-R1-03 | 25 | 0 | 1 | 0 | 0 | 0 | 0
ZONE-R3-Z2W | ROW-R3-Z2W-R1 | 30 |  |  | LL-R3-W | AIRZONE-R3-W1 | RACK-R3-Z2W-R1-04 | POD-05 | RACKPDU-RACK-R3-Z2W-R1-04-A | RACKPDU-RACK-R3-Z2W-R1-04-B | 30 | 22.5 | 7.5 | 36 | 75% | 25% | RPP-R3-A1 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 30 | 22.5 | 7.5 | 0 | 0 | 0 | [9 empty] | 30 | 0 | 30 | 30 | 30 | 30 | 100% | 0% | 100% | 100% | 100% | 100% |  |  | DTC-RACK-R3-Z2W-R1-04 | 25 | 0 | 1 | 0 | 0 | 0 | 0
ZONE-R3-Z2W | ROW-R3-Z2W-R1 | 30 |  |  | LL-R3-W | AIRZONE-R3-W1 | RACK-R3-Z2W-R1-05 | POD-05 | RACKPDU-RACK-R3-Z2W-R1-05-A | RACKPDU-RACK-R3-Z2W-R1-05-B | 30 | 22.5 | 7.5 | 36 | 75% | 25% | RPP-R3-A2 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 30 | 22.5 | 7.5 | 30 | 22.5 | 7.5 | [9 empty] | 30 | 0 | 0 | 30 | 30 | 30 | 100% | 0% | 0% | 100% | 100% | 100% |  |  | DTC-RACK-R3-Z2W-R1-05 | 25 | 0 | 1 | 1 | 0 | 0 | 0
ZONE-R3-Z2W | ROW-R3-Z2W-R1 | 30 |  |  | LL-R3-W | AIRZONE-R3-W1 | RACK-R3-Z2W-R1-06 | POD-05 | RACKPDU-RACK-R3-Z2W-R1-06-A | RACKPDU-RACK-R3-Z2W-R1-06-B | 30 | 22.5 | 7.5 | 36 | 75% | 25% | RPP-R3-A2 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 30 | 22.5 | 7.5 | 30 | 22.5 | 7.5 | [9 empty] | 30 | 0 | 0 | 30 | 30 | 30 | 100% | 0% | 0% | 100% | 100% | 100% |  |  | DTC-RACK-R3-Z2W-R1-06 | 25 | 0 | 1 | 1 | 0 | 0 | 0
ZONE-R3-Z2W | ROW-R3-Z2W-R1 | 30 |  |  | LL-R3-W | AIRZONE-R3-W1 | RACK-R3-Z2W-R1-07 | POD-05 | RACKPDU-RACK-R3-Z2W-R1-07-A | RACKPDU-RACK-R3-Z2W-R1-07-B | 30 | 22.5 | 7.5 | 36 | 75% | 25% | RPP-R3-A2 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 30 | 22.5 | 7.5 | 30 | 22.5 | 7.5 | [9 empty] | 30 | 0 | 0 | 30 | 30 | 30 | 100% | 0% | 0% | 100% | 100% | 100% |  |  | DTC-RACK-R3-Z2W-R1-07 | 25 | 0 | 1 | 1 | 0 | 0 | 0
ZONE-R3-Z2W | ROW-R3-Z2W-R1 | 30 |  |  | LL-R3-W | AIRZONE-R3-W1 | RACK-R3-Z2W-R1-08 | POD-05 | RACKPDU-RACK-R3-Z2W-R1-08-A | RACKPDU-RACK-R3-Z2W-R1-08-B | 30 | 22.5 | 7.5 | 36 | 75% | 25% | RPP-R3-A2 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 30 | 22.5 | 7.5 | 30 | 22.5 | 7.5 | [9 empty] | 30 | 0 | 0 | 30 | 30 | 30 | 100% | 0% | 0% | 100% | 100% | 100% |  |  | DTC-RACK-R3-Z2W-R1-08 | 25 | 0 | 1 | 1 | 0 | 0 | 0
ZONE-R3-Z2W | ROW-R3-Z2W-R1 | 30 |  |  | LL-R3-W | AIRZONE-R3-W1 | RACK-R3-Z2W-R1-09 | POD-05 | RACKPDU-RACK-R3-Z2W-R1-09-A | RACKPDU-RACK-R3-Z2W-R1-09-B | 30 | 22.5 | 7.5 | 36 | 75% | 25% | RPP-R3-A1 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 30 | 22.5 | 7.5 | 30 | 22.5 | 7.5 | [9 empty] | 30 | 0 | 0 | 30 | 30 | 30 | 100% | 0% | 0% | 100% | 100% | 100% |  |  | DTC-RACK-R3-Z2W-R1-09 | 25 | 0 | 1 | 1 | 0 | 0 | 0
ZONE-R3-Z2W | ROW-R3-Z2W-R1 | 30 |  |  | LL-R3-W | AIRZONE-R3-W1 | RACK-R3-Z2W-R1-10 | POD-05 | RACKPDU-RACK-R3-Z2W-R1-10-A | RACKPDU-RACK-R3-Z2W-R1-10-B | 30 | 22.5 | 7.5 | 36 | 75% | 25% | RPP-R3-A1 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 30 | 22.5 | 7.5 | 30 | 22.5 | 7.5 | [9 empty] | 30 | 0 | 0 | 30 | 30 | 30 | 100% | 0% | 0% | 100% | 100% | 100% |  |  | DTC-RACK-R3-Z2W-R1-10 | 25 | 0 | 1 | 1 | 0 | 0 | 0
ZONE-R3-Z2W | ROW-R3-Z2W-R1 | 30 |  |  | LL-R3-W | AIRZONE-R3-W1 | RACK-R3-Z2W-R1-11 | POD-05 | RACKPDU-RACK-R3-Z2W-R1-11-A | RACKPDU-RACK-R3-Z2W-R1-11-B | 30 | 22.5 | 7.5 | 36 | 75% | 25% | RPP-R3-A1 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 30 | 22.5 | 7.5 | 30 | 22.5 | 7.5 | [9 empty] | 30 | 0 | 0 | 30 | 30 | 30 | 100% | 0% | 0% | 100% | 100% | 100% |  |  | DTC-RACK-R3-Z2W-R1-11 | 25 | 0 | 1 | 1 | 0 | 0 | 0
ZONE-R3-Z2W | ROW-R3-Z2W-R1 | 30 |  |  | LL-R3-W | AIRZONE-R3-W1 | RACK-R3-Z2W-R1-12 | POD-05 | RACKPDU-RACK-R3-Z2W-R1-12-A | RACKPDU-RACK-R3-Z2W-R1-12-B | 30 | 22.5 | 7.5 | 36 | 75% | 25% | RPP-R3-A1 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 30 | 22.5 | 7.5 | 30 | 22.5 | 7.5 | [9 empty] | 30 | 0 | 0 | 30 | 30 | 30 | 100% | 0% | 0% | 100% | 100% | 100% |  |  | DTC-RACK-R3-Z2W-R1-12 | 25 | 0 | 1 | 1 | 0 | 0 | 0
ZONE-R3-Z2W | ROW-R3-Z2W-R2 | 30 |  |  | LL-R3-W | AIRZONE-R3-W1 | RACK-R3-Z2W-R2-01 | POD-05 | RACKPDU-RACK-R3-Z2W-R2-01-A | RACKPDU-RACK-R3-Z2W-R2-01-B | 30 | 22.5 | 7.5 | 36 | 75% | 25% | RPP-R3-A2 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 30 | 22.5 | 7.5 | 30 | 22.5 | 7.5 | [9 empty] | 30 | 0 | 0 | 30 | 30 | 30 | 100% | 0% | 0% | 100% | 100% | 100% |  |  | DTC-RACK-R3-Z2W-R2-01 | 25 | 0 | 1 | 1 | 0 | 0 | 0
ZONE-R3-Z2W | ROW-R3-Z2W-R2 | 30 |  |  | LL-R3-W | AIRZONE-R3-W1 | RACK-R3-Z2W-R2-02 | POD-05 | RACKPDU-RACK-R3-Z2W-R2-02-A | RACKPDU-RACK-R3-Z2W-R2-02-B | 30 | 22.5 | 7.5 | 36 | 75% | 25% | RPP-R3-A2 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 30 | 22.5 | 7.5 | 30 | 22.5 | 7.5 | [9 empty] | 30 | 0 | 0 | 30 | 30 | 30 | 100% | 0% | 0% | 100% | 100% | 100% |  |  | DTC-RACK-R3-Z2W-R2-02 | 25 | 0 | 1 | 1 | 0 | 0 | 0
ZONE-R3-Z2W | ROW-R3-Z2W-R2 | 30 |  |  | LL-R3-W | AIRZONE-R3-W1 | RACK-R3-Z2W-R2-03 | POD-05 | RACKPDU-RACK-R3-Z2W-R2-03-A | RACKPDU-RACK-R3-Z2W-R2-03-B | 30 | 22.5 | 7.5 | 36 | 75% | 25% | RPP-R3-A2 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 30 | 22.5 | 7.5 | 30 | 22.5 | 7.5 | [9 empty] | 30 | 0 | 0 | 30 | 30 | 30 | 100% | 0% | 0% | 100% | 100% | 100% |  |  | DTC-RACK-R3-Z2W-R2-03 | 25 | 0 | 1 | 1 | 0 | 0 | 0
ZONE-R3-Z2W | ROW-R3-Z2W-R2 | 30 |  |  | LL-R3-W | AIRZONE-R3-W1 | RACK-R3-Z2W-R2-04 | POD-05 | RACKPDU-RACK-R3-Z2W-R2-04-A | RACKPDU-RACK-R3-Z2W-R2-04-B | 30 | 22.5 | 7.5 | 36 | 75% | 25% | RPP-R3-A2 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 30 | 22.5 | 7.5 | 30 | 22.5 | 7.5 | [9 empty] | 30 | 0 | 0 | 30 | 30 | 30 | 100% | 0% | 0% | 100% | 100% | 100% |  |  | DTC-RACK-R3-Z2W-R2-04 | 25 | 0 | 1 | 1 | 0 | 0 | 0
ZONE-R3-Z2W | ROW-R3-Z2W-R2 | 30 |  |  | LL-R3-W | AIRZONE-R3-W1 | RACK-R3-Z2W-R2-05 | POD-05 | RACKPDU-RACK-R3-Z2W-R2-05-A | RACKPDU-RACK-R3-Z2W-R2-05-B | 30 | 22.5 | 7.5 | 36 | 75% | 25% | RPP-R3-A1 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 30 | 22.5 | 7.5 | 0 | 0 | 0 | [9 empty] | 30 | 0 | 30 | 30 | 30 | 30 | 100% | 0% | 100% | 100% | 100% | 100% |  |  | DTC-RACK-R3-Z2W-R2-05 | 25 | 0 | 1 | 0 | 0 | 0 | 0
ZONE-R3-Z2W | ROW-R3-Z2W-R2 | 30 |  |  | LL-R3-W | AIRZONE-R3-W1 | RACK-R3-Z2W-R2-06 | POD-05 | RACKPDU-RACK-R3-Z2W-R2-06-A | RACKPDU-RACK-R3-Z2W-R2-06-B | 30 | 22.5 | 7.5 | 36 | 75% | 25% | RPP-R3-A1 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 30 | 22.5 | 7.5 | 0 | 0 | 0 | [9 empty] | 30 | 0 | 30 | 30 | 30 | 30 | 100% | 0% | 100% | 100% | 100% | 100% |  |  | DTC-RACK-R3-Z2W-R2-06 | 25 | 0 | 1 | 0 | 0 | 0 | 0
ZONE-R3-Z2W | ROW-R3-Z2W-R2 | 30 |  |  | LL-R3-W | AIRZONE-R3-W1 | RACK-R3-Z2W-R2-07 | POD-05 | RACKPDU-RACK-R3-Z2W-R2-07-A | RACKPDU-RACK-R3-Z2W-R2-07-B | 30 | 22.5 | 7.5 | 36 | 75% | 25% | RPP-R3-A1 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 30 | 22.5 | 7.5 | 0 | 0 | 0 | [9 empty] | 30 | 0 | 30 | 30 | 30 | 30 | 100% | 0% | 100% | 100% | 100% | 100% |  |  | DTC-RACK-R3-Z2W-R2-07 | 25 | 0 | 1 | 0 | 0 | 0 | 0
ZONE-R3-Z2W | ROW-R3-Z2W-R2 | 30 |  |  | LL-R3-W | AIRZONE-R3-W1 | RACK-R3-Z2W-R2-08 | POD-05 | RACKPDU-RACK-R3-Z2W-R2-08-A | RACKPDU-RACK-R3-Z2W-R2-08-B | 30 | 22.5 | 7.5 | 36 | 75% | 25% | RPP-R3-A1 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 30 | 22.5 | 7.5 | 0 | 0 | 0 | [9 empty] | 30 | 0 | 30 | 30 | 30 | 30 | 100% | 0% | 100% | 100% | 100% | 100% |  |  | DTC-RACK-R3-Z2W-R2-08 | 25 | 0 | 1 | 0 | 0 | 0 | 0
ZONE-R3-Z2W | ROW-R3-Z2W-R2 | 30 |  |  | LL-R3-W | AIRZONE-R3-W1 | RACK-R3-Z2W-R2-09 | POD-05 | RACKPDU-RACK-R3-Z2W-R2-09-A | RACKPDU-RACK-R3-Z2W-R2-09-B | 30 | 22.5 | 7.5 | 36 | 75% | 25% | RPP-R3-A2 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 30 | 22.5 | 7.5 | 0 | 0 | 0 | [9 empty] | 30 | 0 | 30 | 30 | 30 | 30 | 100% | 0% | 100% | 100% | 100% | 100% |  |  | DTC-RACK-R3-Z2W-R2-09 | 25 | 0 | 1 | 0 | 0 | 0 | 0
ZONE-R3-Z2W | ROW-R3-Z2W-R2 | 30 |  |  | LL-R3-W | AIRZONE-R3-W1 | RACK-R3-Z2W-R2-10 | POD-05 | RACKPDU-RACK-R3-Z2W-R2-10-A | RACKPDU-RACK-R3-Z2W-R2-10-B | 30 | 22.5 | 7.5 | 36 | 75% | 25% | RPP-R3-A2 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 30 | 22.5 | 7.5 | 0 | 0 | 0 | [9 empty] | 30 | 0 | 30 | 30 | 30 | 30 | 100% | 0% | 100% | 100% | 100% | 100% |  |  | DTC-RACK-R3-Z2W-R2-10 | 25 | 0 | 1 | 0 | 0 | 0 | 0
ZONE-R3-Z2W | ROW-R3-Z2W-R2 | 30 |  |  | LL-R3-W | AIRZONE-R3-W1 | RACK-R3-Z2W-R2-11 | POD-05 | RACKPDU-RACK-R3-Z2W-R2-11-A | RACKPDU-RACK-R3-Z2W-R2-11-B | 30 | 22.5 | 7.5 | 36 | 75% | 25% | RPP-R3-A2 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 30 | 22.5 | 7.5 | 0 | 0 | 0 | [9 empty] | 30 | 0 | 30 | 30 | 30 | 30 | 100% | 0% | 100% | 100% | 100% | 100% |  |  | DTC-RACK-R3-Z2W-R2-11 | 25 | 0 | 1 | 0 | 0 | 0 | 0
ZONE-R3-Z2W | ROW-R3-Z2W-R2 | 30 |  |  | LL-R3-W | AIRZONE-R3-W1 | RACK-R3-Z2W-R2-12 | POD-05 | RACKPDU-RACK-R3-Z2W-R2-12-A | RACKPDU-RACK-R3-Z2W-R2-12-B | 30 | 22.5 | 7.5 | 36 | 75% | 25% | RPP-R3-A2 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 30 | 22.5 | 7.5 | 0 | 0 | 0 | [9 empty] | 30 | 0 | 30 | 30 | 30 | 30 | 100% | 0% | 100% | 100% | 100% | 100% |  |  | DTC-RACK-R3-Z2W-R2-12 | 25 | 0 | 1 | 0 | 0 | 0 | 0
ZONE-R3-Z3W | ROW-R3-Z3W-R1 | 30 |  |  | LL-R3-W | AIRZONE-R3-W2 | RACK-R3-Z3W-R1-01 | POD-05 | RACKPDU-RACK-R3-Z3W-R1-01-A | RACKPDU-RACK-R3-Z3W-R1-01-B | 30 | 22.5 | 7.5 | 36 | 75% | 25% | RPP-R3-A1 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 30 | 22.5 | 7.5 | 30 | 22.5 | 7.5 | [9 empty] | 30 | 0 | 0 | 30 | 30 | 30 | 100% | 0% | 0% | 100% | 100% | 100% |  |  | DTC-RACK-R3-Z3W-R1-01 | 25 | 0 | 1 | 1 | 0 | 0 | 0
ZONE-R3-Z3W | ROW-R3-Z3W-R1 | 30 |  |  | LL-R3-W | AIRZONE-R3-W2 | RACK-R3-Z3W-R1-02 | POD-05 | RACKPDU-RACK-R3-Z3W-R1-02-A | RACKPDU-RACK-R3-Z3W-R1-02-B | 30 | 22.5 | 7.5 | 36 | 75% | 25% | RPP-R3-A1 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 30 | 22.5 | 7.5 | 30 | 22.5 | 7.5 | [9 empty] | 30 | 0 | 0 | 30 | 30 | 30 | 100% | 0% | 0% | 100% | 100% | 100% |  |  | DTC-RACK-R3-Z3W-R1-02 | 25 | 0 | 1 | 1 | 0 | 0 | 0
ZONE-R3-Z3W | ROW-R3-Z3W-R1 | 30 |  |  | LL-R3-W | AIRZONE-R3-W2 | RACK-R3-Z3W-R1-03 | POD-05 | RACKPDU-RACK-R3-Z3W-R1-03-A | RACKPDU-RACK-R3-Z3W-R1-03-B | 30 | 22.5 | 7.5 | 36 | 75% | 25% | RPP-R3-A1 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 30 | 22.5 | 7.5 | 30 | 22.5 | 7.5 | [9 empty] | 30 | 0 | 0 | 30 | 30 | 30 | 100% | 0% | 0% | 100% | 100% | 100% |  |  | DTC-RACK-R3-Z3W-R1-03 | 25 | 0 | 1 | 1 | 0 | 0 | 0
ZONE-R3-Z3W | ROW-R3-Z3W-R1 | 30 |  |  | LL-R3-W | AIRZONE-R3-W2 | RACK-R3-Z3W-R1-04 | POD-05 | RACKPDU-RACK-R3-Z3W-R1-04-A | RACKPDU-RACK-R3-Z3W-R1-04-B | 30 | 22.5 | 7.5 | 36 | 75% | 25% | RPP-R3-A1 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 30 | 22.5 | 7.5 | 30 | 22.5 | 7.5 | [9 empty] | 30 | 0 | 0 | 30 | 30 | 30 | 100% | 0% | 0% | 100% | 100% | 100% |  |  | DTC-RACK-R3-Z3W-R1-04 | 25 | 0 | 1 | 1 | 0 | 0 | 0
ZONE-R3-Z3W | ROW-R3-Z3W-R1 | 30 |  |  | LL-R3-W | AIRZONE-R3-W2 | RACK-R3-Z3W-R1-05 | POD-05 | RACKPDU-RACK-R3-Z3W-R1-05-A | RACKPDU-RACK-R3-Z3W-R1-05-B | 30 | 22.5 | 7.5 | 36 | 75% | 25% | RPP-R3-A2 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 30 | 22.5 | 7.5 | 30 | 22.5 | 7.5 | [9 empty] | 30 | 0 | 0 | 30 | 30 | 30 | 100% | 0% | 0% | 100% | 100% | 100% |  |  | DTC-RACK-R3-Z3W-R1-05 | 25 | 0 | 1 | 1 | 0 | 0 | 0
ZONE-R3-Z3W | ROW-R3-Z3W-R1 | 30 |  |  | LL-R3-W | AIRZONE-R3-W2 | RACK-R3-Z3W-R1-06 | POD-05 | RACKPDU-RACK-R3-Z3W-R1-06-A | RACKPDU-RACK-R3-Z3W-R1-06-B | 30 | 22.5 | 7.5 | 36 | 75% | 25% | RPP-R3-A2 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 30 | 22.5 | 7.5 | 30 | 22.5 | 7.5 | [9 empty] | 30 | 0 | 0 | 30 | 30 | 30 | 100% | 0% | 0% | 100% | 100% | 100% |  |  | DTC-RACK-R3-Z3W-R1-06 | 25 | 0 | 1 | 1 | 0 | 0 | 0
ZONE-R3-Z3W | ROW-R3-Z3W-R1 | 30 |  |  | LL-R3-W | AIRZONE-R3-W2 | RACK-R3-Z3W-R1-07 | POD-05 | RACKPDU-RACK-R3-Z3W-R1-07-A | RACKPDU-RACK-R3-Z3W-R1-07-B | 30 | 22.5 | 7.5 | 36 | 75% | 25% | RPP-R3-A2 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 30 | 22.5 | 7.5 | 30 | 22.5 | 7.5 | [9 empty] | 30 | 0 | 0 | 30 | 30 | 30 | 100% | 0% | 0% | 100% | 100% | 100% |  |  | DTC-RACK-R3-Z3W-R1-07 | 25 | 0 | 1 | 1 | 0 | 0 | 0
ZONE-R3-Z3W | ROW-R3-Z3W-R1 | 30 |  |  | LL-R3-W | AIRZONE-R3-W2 | RACK-R3-Z3W-R1-08 | POD-05 | RACKPDU-RACK-R3-Z3W-R1-08-A | RACKPDU-RACK-R3-Z3W-R1-08-B | 30 | 22.5 | 7.5 | 36 | 75% | 25% | RPP-R3-A2 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 30 | 22.5 | 7.5 | 30 | 22.5 | 7.5 | [9 empty] | 30 | 0 | 0 | 30 | 30 | 30 | 100% | 0% | 0% | 100% | 100% | 100% |  |  | DTC-RACK-R3-Z3W-R1-08 | 25 | 0 | 1 | 1 | 0 | 0 | 0
ZONE-R3-Z3W | ROW-R3-Z3W-R1 | 30 |  |  | LL-R3-W | AIRZONE-R3-W2 | RACK-R3-Z3W-R1-09 | POD-05 | RACKPDU-RACK-R3-Z3W-R1-09-A | RACKPDU-RACK-R3-Z3W-R1-09-B | 30 | 22.5 | 7.5 | 36 | 75% | 25% | RPP-R3-A1 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 30 | 22.5 | 7.5 | 30 | 22.5 | 7.5 | [9 empty] | 30 | 0 | 0 | 30 | 30 | 30 | 100% | 0% | 0% | 100% | 100% | 100% |  |  | DTC-RACK-R3-Z3W-R1-09 | 25 | 0 | 1 | 1 | 0 | 0 | 0
ZONE-R3-Z3W | ROW-R3-Z3W-R1 | 30 |  |  | LL-R3-W | AIRZONE-R3-W2 | RACK-R3-Z3W-R1-10 | POD-05 | RACKPDU-RACK-R3-Z3W-R1-10-A | RACKPDU-RACK-R3-Z3W-R1-10-B | 30 | 22.5 | 7.5 | 36 | 75% | 25% | RPP-R3-A1 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 30 | 22.5 | 7.5 | 30 | 22.5 | 7.5 | [9 empty] | 30 | 0 | 0 | 30 | 30 | 30 | 100% | 0% | 0% | 100% | 100% | 100% |  |  | DTC-RACK-R3-Z3W-R1-10 | 25 | 0 | 1 | 1 | 0 | 0 | 0
ZONE-R3-Z3W | ROW-R3-Z3W-R1 | 30 |  |  | LL-R3-W | AIRZONE-R3-W2 | RACK-R3-Z3W-R1-11 | POD-05 | RACKPDU-RACK-R3-Z3W-R1-11-A | RACKPDU-RACK-R3-Z3W-R1-11-B | 30 | 22.5 | 7.5 | 36 | 75% | 25% | RPP-R3-A1 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 30 | 22.5 | 7.5 | 30 | 22.5 | 7.5 | [9 empty] | 30 | 0 | 0 | 30 | 30 | 30 | 100% | 0% | 0% | 100% | 100% | 100% |  |  | DTC-RACK-R3-Z3W-R1-11 | 25 | 0 | 1 | 1 | 0 | 0 | 0
ZONE-R3-Z3W | ROW-R3-Z3W-R1 | 30 |  |  | LL-R3-W | AIRZONE-R3-W2 | RACK-R3-Z3W-R1-12 | POD-05 | RACKPDU-RACK-R3-Z3W-R1-12-A | RACKPDU-RACK-R3-Z3W-R1-12-B | 30 | 22.5 | 7.5 | 36 | 75% | 25% | RPP-R3-A1 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 30 | 22.5 | 7.5 | 30 | 22.5 | 7.5 | [9 empty] | 30 | 0 | 0 | 30 | 30 | 30 | 100% | 0% | 0% | 100% | 100% | 100% |  |  | DTC-RACK-R3-Z3W-R1-12 | 25 | 0 | 1 | 1 | 0 | 0 | 0
ZONE-R3-Z3W | ROW-R3-Z3W-R2 | 30 |  |  | LL-R3-W | AIRZONE-R3-W2 | RACK-R3-Z3W-R2-01 | POD-05 | RACKPDU-RACK-R3-Z3W-R2-01-A | RACKPDU-RACK-R3-Z3W-R2-01-B | 30 | 22.5 | 7.5 | 36 | 75% | 25% | RPP-R3-A2 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 30 | 22.5 | 7.5 | [9 empty] | 30 | 30 | 0 | 30 | 30 | 30 | 100% | 100% | 0% | 100% | 100% | 100% |  |  | DTC-RACK-R3-Z3W-R2-01 | 25 | 0 | 0 | 1 | 0 | 0 | 0
ZONE-R3-Z3W | ROW-R3-Z3W-R2 | 30 |  |  | LL-R3-W | AIRZONE-R3-W2 | RACK-R3-Z3W-R2-02 | POD-05 | RACKPDU-RACK-R3-Z3W-R2-02-A | RACKPDU-RACK-R3-Z3W-R2-02-B | 30 | 22.5 | 7.5 | 36 | 75% | 25% | RPP-R3-A2 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 30 | 22.5 | 7.5 | [9 empty] | 30 | 30 | 0 | 30 | 30 | 30 | 100% | 100% | 0% | 100% | 100% | 100% |  |  | DTC-RACK-R3-Z3W-R2-02 | 25 | 0 | 0 | 1 | 0 | 0 | 0
ZONE-R3-Z3W | ROW-R3-Z3W-R2 | 30 |  |  | LL-R3-W | AIRZONE-R3-W2 | RACK-R3-Z3W-R2-03 | POD-05 | RACKPDU-RACK-R3-Z3W-R2-03-A | RACKPDU-RACK-R3-Z3W-R2-03-B | 30 | 22.5 | 7.5 | 36 | 75% | 25% | RPP-R3-A2 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 30 | 22.5 | 7.5 | [9 empty] | 30 | 30 | 0 | 30 | 30 | 30 | 100% | 100% | 0% | 100% | 100% | 100% |  |  | DTC-RACK-R3-Z3W-R2-03 | 25 | 0 | 0 | 1 | 0 | 0 | 0
ZONE-R3-Z3W | ROW-R3-Z3W-R2 | 30 |  |  | LL-R3-W | AIRZONE-R3-W2 | RACK-R3-Z3W-R2-04 | POD-05 | RACKPDU-RACK-R3-Z3W-R2-04-A | RACKPDU-RACK-R3-Z3W-R2-04-B | 30 | 22.5 | 7.5 | 36 | 75% | 25% | RPP-R3-A2 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 30 | 22.5 | 7.5 | [9 empty] | 30 | 30 | 0 | 30 | 30 | 30 | 100% | 100% | 0% | 100% | 100% | 100% |  |  | DTC-RACK-R3-Z3W-R2-04 | 25 | 0 | 0 | 1 | 0 | 0 | 0
ZONE-R3-Z3W | ROW-R3-Z3W-R2 | 30 |  |  | LL-R3-W | AIRZONE-R3-W2 | RACK-R3-Z3W-R2-05 | POD-05 | RACKPDU-RACK-R3-Z3W-R2-05-A | RACKPDU-RACK-R3-Z3W-R2-05-B | 30 | 22.5 | 7.5 | 36 | 75% | 25% | RPP-R3-A1 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 30 | 22.5 | 7.5 | [9 empty] | 30 | 30 | 0 | 30 | 30 | 30 | 100% | 100% | 0% | 100% | 100% | 100% |  |  | DTC-RACK-R3-Z3W-R2-05 | 25 | 0 | 0 | 1 | 0 | 0 | 0
ZONE-R3-Z3W | ROW-R3-Z3W-R2 | 30 |  |  | LL-R3-W | AIRZONE-R3-W2 | RACK-R3-Z3W-R2-06 | POD-05 | RACKPDU-RACK-R3-Z3W-R2-06-A | RACKPDU-RACK-R3-Z3W-R2-06-B | 30 | 22.5 | 7.5 | 36 | 75% | 25% | RPP-R3-A1 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 30 | 22.5 | 7.5 | [9 empty] | 30 | 30 | 0 | 30 | 30 | 30 | 100% | 100% | 0% | 100% | 100% | 100% |  |  | DTC-RACK-R3-Z3W-R2-06 | 25 | 0 | 0 | 1 | 0 | 0 | 0
ZONE-R3-Z3W | ROW-R3-Z3W-R2 | 30 |  |  | LL-R3-W | AIRZONE-R3-W2 | RACK-R3-Z3W-R2-07 | POD-05 | RACKPDU-RACK-R3-Z3W-R2-07-A | RACKPDU-RACK-R3-Z3W-R2-07-B | 30 | 22.5 | 7.5 | 36 | 75% | 25% | RPP-R3-A1 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 30 | 22.5 | 7.5 | [9 empty] | 30 | 30 | 0 | 30 | 30 | 30 | 100% | 100% | 0% | 100% | 100% | 100% |  |  | DTC-RACK-R3-Z3W-R2-07 | 25 | 0 | 0 | 1 | 0 | 0 | 0
ZONE-R3-Z3W | ROW-R3-Z3W-R2 | 30 |  |  | LL-R3-W | AIRZONE-R3-W2 | RACK-R3-Z3W-R2-08 | POD-05 | RACKPDU-RACK-R3-Z3W-R2-08-A | RACKPDU-RACK-R3-Z3W-R2-08-B | 30 | 22.5 | 7.5 | 36 | 75% | 25% | RPP-R3-A1 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 30 | 22.5 | 7.5 | [9 empty] | 30 | 30 | 0 | 30 | 30 | 30 | 100% | 100% | 0% | 100% | 100% | 100% |  |  | DTC-RACK-R3-Z3W-R2-08 | 25 | 0 | 0 | 1 | 0 | 0 | 0
ZONE-R3-Z3W | ROW-R3-Z3W-R2 | 30 |  |  | LL-R3-W | AIRZONE-R3-W2 | RACK-R3-Z3W-R2-09 | POD-05 | RACKPDU-RACK-R3-Z3W-R2-09-A | RACKPDU-RACK-R3-Z3W-R2-09-B | 30 | 22.5 | 7.5 | 36 | 75% | 25% | RPP-R3-A2 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 30 | 22.5 | 7.5 | [9 empty] | 30 | 30 | 0 | 30 | 30 | 30 | 100% | 100% | 0% | 100% | 100% | 100% |  |  | DTC-RACK-R3-Z3W-R2-09 | 25 | 0 | 0 | 1 | 0 | 0 | 0
ZONE-R3-Z3W | ROW-R3-Z3W-R2 | 30 |  |  | LL-R3-W | AIRZONE-R3-W2 | RACK-R3-Z3W-R2-10 | POD-05 | RACKPDU-RACK-R3-Z3W-R2-10-A | RACKPDU-RACK-R3-Z3W-R2-10-B | 30 | 22.5 | 7.5 | 36 | 75% | 25% | RPP-R3-A2 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 30 | 22.5 | 7.5 | [9 empty] | 30 | 30 | 0 | 30 | 30 | 30 | 100% | 100% | 0% | 100% | 100% | 100% |  |  | DTC-RACK-R3-Z3W-R2-10 | 25 | 0 | 0 | 1 | 0 | 0 | 0
ZONE-R3-Z3W | ROW-R3-Z3W-R2 | 30 |  |  | LL-R3-W | AIRZONE-R3-W2 | RACK-R3-Z3W-R2-11 | POD-05 | RACKPDU-RACK-R3-Z3W-R2-11-A | RACKPDU-RACK-R3-Z3W-R2-11-B | 30 | 22.5 | 7.5 | 36 | 75% | 25% | RPP-R3-A2 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 100% | 100% | 100% | 100% | 100% | 100% |  |  | DTC-RACK-R3-Z3W-R2-11 | 25 | 0 | 0 | 0 | 0 | 0 | 0
ZONE-R3-Z3W | ROW-R3-Z3W-R2 | 30 |  |  | LL-R3-W | AIRZONE-R3-W2 | RACK-R3-Z3W-R2-12 | POD-05 | RACKPDU-RACK-R3-Z3W-R2-12-A | RACKPDU-RACK-R3-Z3W-R2-12-B | 30 | 22.5 | 7.5 | 36 | 75% | 25% | RPP-R3-A2 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 100% | 100% | 100% | 100% | 100% | 100% |  |  | DTC-RACK-R3-Z3W-R2-12 | 25 | 0 | 0 | 0 | 0 | 0 | 0
ZONE-R3-Z4E | ROW-R3-Z4E-R1 | 45 |  |  | LL-R3-E | AIRZONE-R3-E1 | RACK-R3-Z4E-R1-01 | POD-06 | RACKPDU-RACK-R3-Z4E-R1-01-A | RACKPDU-RACK-R3-Z4E-R1-01-B | 45 | 38.25 | 6.75 | 54 | 85% | 15% | RPP-R3-A1 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 30 | 25.5 | 4.5 |  |  |  | 45 | 45 | 45 | 45 | 15 | 45 | 100% | 100% | 100% | 100% | 33.33% | 100% |  |  | DTC-RACK-R3-Z4E-R1-01 | 42.5 | 0 | 0 | 0 | 0 | 1 | 0
ZONE-R3-Z4E | ROW-R3-Z4E-R1 | 45 |  |  | LL-R3-E | AIRZONE-R3-E1 | RACK-R3-Z4E-R1-02 | POD-06 | RACKPDU-RACK-R3-Z4E-R1-02-A | RACKPDU-RACK-R3-Z4E-R1-02-B | 45 | 38.25 | 6.75 | 54 | 85% | 15% | RPP-R3-A1 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 30 | 25.5 | 4.5 |  |  |  | 45 | 45 | 45 | 45 | 15 | 45 | 100% | 100% | 100% | 100% | 33.33% | 100% |  |  | DTC-RACK-R3-Z4E-R1-02 | 42.5 | 0 | 0 | 0 | 0 | 1 | 0
ZONE-R3-Z4E | ROW-R3-Z4E-R1 | 45 |  |  | LL-R3-E | AIRZONE-R3-E1 | RACK-R3-Z4E-R1-03 | POD-06 | RACKPDU-RACK-R3-Z4E-R1-03-A | RACKPDU-RACK-R3-Z4E-R1-03-B | 45 | 38.25 | 6.75 | 54 | 85% | 15% | RPP-R3-A1 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 30 | 25.5 | 4.5 |  |  |  | 45 | 45 | 45 | 45 | 15 | 45 | 100% | 100% | 100% | 100% | 33.33% | 100% |  |  | DTC-RACK-R3-Z4E-R1-03 | 42.5 | 0 | 0 | 0 | 0 | 1 | 0
ZONE-R3-Z4E | ROW-R3-Z4E-R1 | 45 |  |  | LL-R3-E | AIRZONE-R3-E1 | RACK-R3-Z4E-R1-04 | POD-06 | RACKPDU-RACK-R3-Z4E-R1-04-A | RACKPDU-RACK-R3-Z4E-R1-04-B | 45 | 38.25 | 6.75 | 54 | 85% | 15% | RPP-R3-A1 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 30 | 25.5 | 4.5 |  |  |  | 45 | 45 | 45 | 45 | 15 | 45 | 100% | 100% | 100% | 100% | 33.33% | 100% |  |  | DTC-RACK-R3-Z4E-R1-04 | 42.5 | 0 | 0 | 0 | 0 | 1 | 0
ZONE-R3-Z4E | ROW-R3-Z4E-R1 | 45 |  |  | LL-R3-E | AIRZONE-R3-E1 | RACK-R3-Z4E-R1-05 | POD-06 | RACKPDU-RACK-R3-Z4E-R1-05-A | RACKPDU-RACK-R3-Z4E-R1-05-B | 45 | 38.25 | 6.75 | 54 | 85% | 15% | RPP-R3-A3 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 25.5 | 4.5 | 30 | 25.5 | 4.5 |  |  |  | 45 | 45 | 45 | 15 | 15 | 45 | 100% | 100% | 100% | 33.33% | 33.33% | 100% |  |  | DTC-RACK-R3-Z4E-R1-05 | 42.5 | 0 | 0 | 0 | 1 | 1 | 0
ZONE-R3-Z4E | ROW-R3-Z4E-R1 | 45 |  |  | LL-R3-E | AIRZONE-R3-E1 | RACK-R3-Z4E-R1-06 | POD-06 | RACKPDU-RACK-R3-Z4E-R1-06-A | RACKPDU-RACK-R3-Z4E-R1-06-B | 45 | 38.25 | 6.75 | 54 | 85% | 15% | RPP-R3-A3 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 25.5 | 4.5 | 30 | 25.5 | 4.5 |  |  |  | 45 | 45 | 45 | 15 | 15 | 45 | 100% | 100% | 100% | 33.33% | 33.33% | 100% |  |  | DTC-RACK-R3-Z4E-R1-06 | 42.5 | 0 | 0 | 0 | 1 | 1 | 0
ZONE-R3-Z4E | ROW-R3-Z4E-R1 | 45 |  |  | LL-R3-E | AIRZONE-R3-E1 | RACK-R3-Z4E-R1-07 | POD-06 | RACKPDU-RACK-R3-Z4E-R1-07-A | RACKPDU-RACK-R3-Z4E-R1-07-B | 45 | 38.25 | 6.75 | 54 | 85% | 15% | RPP-R3-A3 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 25.5 | 4.5 | 30 | 25.5 | 4.5 |  |  |  | 45 | 45 | 45 | 15 | 15 | 45 | 100% | 100% | 100% | 33.33% | 33.33% | 100% |  |  | DTC-RACK-R3-Z4E-R1-07 | 42.5 | 0 | 0 | 0 | 1 | 1 | 0
ZONE-R3-Z4E | ROW-R3-Z4E-R1 | 45 |  |  | LL-R3-E | AIRZONE-R3-E1 | RACK-R3-Z4E-R1-08 | POD-06 | RACKPDU-RACK-R3-Z4E-R1-08-A | RACKPDU-RACK-R3-Z4E-R1-08-B | 45 | 38.25 | 6.75 | 54 | 85% | 15% | RPP-R3-A3 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 25.5 | 4.5 | 30 | 25.5 | 4.5 |  |  |  | 45 | 45 | 45 | 15 | 15 | 45 | 100% | 100% | 100% | 33.33% | 33.33% | 100% |  |  | DTC-RACK-R3-Z4E-R1-08 | 42.5 | 0 | 0 | 0 | 1 | 1 | 0
ZONE-R3-Z4E | ROW-R3-Z4E-R1 | 45 |  |  | LL-R3-E | AIRZONE-R3-E1 | RACK-R3-Z4E-R1-09 | POD-06 | RACKPDU-RACK-R3-Z4E-R1-09-A | RACKPDU-RACK-R3-Z4E-R1-09-B | 45 | 38.25 | 6.75 | 54 | 85% | 15% | RPP-R3-A3 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 25.5 | 4.5 | 30 | 25.5 | 4.5 |  |  |  | 45 | 45 | 45 | 15 | 15 | 45 | 100% | 100% | 100% | 33.33% | 33.33% | 100% |  |  | DTC-RACK-R3-Z4E-R1-09 | 42.5 | 0 | 0 | 0 | 1 | 1 | 0
ZONE-R3-Z4E | ROW-R3-Z4E-R1 | 45 |  |  | LL-R3-E | AIRZONE-R3-E1 | RACK-R3-Z4E-R1-10 | POD-06 | RACKPDU-RACK-R3-Z4E-R1-10-A | RACKPDU-RACK-R3-Z4E-R1-10-B | 45 | 38.25 | 6.75 | 54 | 85% | 15% | RPP-R3-A3 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 25.5 | 4.5 | 30 | 25.5 | 4.5 |  |  |  | 45 | 45 | 45 | 15 | 15 | 45 | 100% | 100% | 100% | 33.33% | 33.33% | 100% |  |  | DTC-RACK-R3-Z4E-R1-10 | 42.5 | 0 | 0 | 0 | 1 | 1 | 0
ZONE-R3-Z4E | ROW-R3-Z4E-R1 | 45 |  |  | LL-R3-E | AIRZONE-R3-E1 | RACK-R3-Z4E-R1-11 | POD-06 | RACKPDU-RACK-R3-Z4E-R1-11-A | RACKPDU-RACK-R3-Z4E-R1-11-B | 45 | 38.25 | 6.75 | 54 | 85% | 15% | RPP-R3-A3 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 25.5 | 4.5 | 30 | 25.5 | 4.5 |  |  |  | 45 | 45 | 45 | 15 | 15 | 45 | 100% | 100% | 100% | 33.33% | 33.33% | 100% |  |  | DTC-RACK-R3-Z4E-R1-11 | 42.5 | 0 | 0 | 0 | 1 | 1 | 0
ZONE-R3-Z4E | ROW-R3-Z4E-R1 | 45 |  |  | LL-R3-E | AIRZONE-R3-E1 | RACK-R3-Z4E-R1-12 | POD-06 | RACKPDU-RACK-R3-Z4E-R1-12-A | RACKPDU-RACK-R3-Z4E-R1-12-B | 45 | 38.25 | 6.75 | 54 | 85% | 15% | RPP-R3-A3 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 25.5 | 4.5 | 30 | 25.5 | 4.5 |  |  |  | 45 | 45 | 45 | 15 | 15 | 45 | 100% | 100% | 100% | 33.33% | 33.33% | 100% |  |  | DTC-RACK-R3-Z4E-R1-12 | 42.5 | 0 | 0 | 0 | 1 | 1 | 0
ZONE-R3-Z4E | ROW-R3-Z4E-R2 | 45 |  |  | LL-R3-E | AIRZONE-R3-E1 | RACK-R3-Z4E-R2-01 | POD-06 | RACKPDU-RACK-R3-Z4E-R2-01-A | RACKPDU-RACK-R3-Z4E-R2-01-B | 45 | 38.25 | 6.75 | 54 | 85% | 15% | RPP-R3-A2 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 30 | 25.5 | 4.5 |  |  |  | 45 | 45 | 45 | 45 | 15 | 45 | 100% | 100% | 100% | 100% | 33.33% | 100% |  |  | DTC-RACK-R3-Z4E-R2-01 | 42.5 | 0 | 0 | 0 | 0 | 1 | 0
ZONE-R3-Z4E | ROW-R3-Z4E-R2 | 45 |  |  | LL-R3-E | AIRZONE-R3-E1 | RACK-R3-Z4E-R2-02 | POD-06 | RACKPDU-RACK-R3-Z4E-R2-02-A | RACKPDU-RACK-R3-Z4E-R2-02-B | 45 | 38.25 | 6.75 | 54 | 85% | 15% | RPP-R3-A2 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 30 | 25.5 | 4.5 |  |  |  | 45 | 45 | 45 | 45 | 15 | 45 | 100% | 100% | 100% | 100% | 33.33% | 100% |  |  | DTC-RACK-R3-Z4E-R2-02 | 42.5 | 0 | 0 | 0 | 0 | 1 | 0
ZONE-R3-Z4E | ROW-R3-Z4E-R2 | 45 |  |  | LL-R3-E | AIRZONE-R3-E1 | RACK-R3-Z4E-R2-03 | POD-06 | RACKPDU-RACK-R3-Z4E-R2-03-A | RACKPDU-RACK-R3-Z4E-R2-03-B | 45 | 38.25 | 6.75 | 54 | 85% | 15% | RPP-R3-A2 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 30 | 25.5 | 4.5 |  |  |  | 45 | 45 | 45 | 45 | 15 | 45 | 100% | 100% | 100% | 100% | 33.33% | 100% |  |  | DTC-RACK-R3-Z4E-R2-03 | 42.5 | 0 | 0 | 0 | 0 | 1 | 0
ZONE-R3-Z4E | ROW-R3-Z4E-R2 | 45 |  |  | LL-R3-E | AIRZONE-R3-E1 | RACK-R3-Z4E-R2-04 | POD-06 | RACKPDU-RACK-R3-Z4E-R2-04-A | RACKPDU-RACK-R3-Z4E-R2-04-B | 45 | 38.25 | 6.75 | 54 | 85% | 15% | RPP-R3-A2 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 30 | 25.5 | 4.5 |  |  |  | 45 | 45 | 45 | 45 | 15 | 45 | 100% | 100% | 100% | 100% | 33.33% | 100% |  |  | DTC-RACK-R3-Z4E-R2-04 | 42.5 | 0 | 0 | 0 | 0 | 1 | 0
ZONE-R3-Z4E | ROW-R3-Z4E-R2 | 45 |  |  | LL-R3-E | AIRZONE-R3-E1 | RACK-R3-Z4E-R2-05 | POD-06 | RACKPDU-RACK-R3-Z4E-R2-05-A | RACKPDU-RACK-R3-Z4E-R2-05-B | 45 | 38.25 | 6.75 | 54 | 85% | 15% | RPP-R3-A4 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 25.5 | 4.5 | 30 | 25.5 | 4.5 |  |  |  | 45 | 45 | 45 | 15 | 15 | 45 | 100% | 100% | 100% | 33.33% | 33.33% | 100% |  |  | DTC-RACK-R3-Z4E-R2-05 | 42.5 | 0 | 0 | 0 | 1 | 1 | 0
ZONE-R3-Z4E | ROW-R3-Z4E-R2 | 45 |  |  | LL-R3-E | AIRZONE-R3-E1 | RACK-R3-Z4E-R2-06 | POD-06 | RACKPDU-RACK-R3-Z4E-R2-06-A | RACKPDU-RACK-R3-Z4E-R2-06-B | 45 | 38.25 | 6.75 | 54 | 85% | 15% | RPP-R3-A4 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 25.5 | 4.5 | 30 | 25.5 | 4.5 |  |  |  | 45 | 45 | 45 | 15 | 15 | 45 | 100% | 100% | 100% | 33.33% | 33.33% | 100% |  |  | DTC-RACK-R3-Z4E-R2-06 | 42.5 | 0 | 0 | 0 | 1 | 1 | 0
ZONE-R3-Z4E | ROW-R3-Z4E-R2 | 45 |  |  | LL-R3-E | AIRZONE-R3-E1 | RACK-R3-Z4E-R2-07 | POD-06 | RACKPDU-RACK-R3-Z4E-R2-07-A | RACKPDU-RACK-R3-Z4E-R2-07-B | 45 | 38.25 | 6.75 | 54 | 85% | 15% | RPP-R3-A4 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 25.5 | 4.5 | 30 | 25.5 | 4.5 |  |  |  | 45 | 45 | 45 | 15 | 15 | 45 | 100% | 100% | 100% | 33.33% | 33.33% | 100% |  |  | DTC-RACK-R3-Z4E-R2-07 | 42.5 | 0 | 0 | 0 | 1 | 1 | 0
ZONE-R3-Z4E | ROW-R3-Z4E-R2 | 45 |  |  | LL-R3-E | AIRZONE-R3-E1 | RACK-R3-Z4E-R2-08 | POD-06 | RACKPDU-RACK-R3-Z4E-R2-08-A | RACKPDU-RACK-R3-Z4E-R2-08-B | 45 | 38.25 | 6.75 | 54 | 85% | 15% | RPP-R3-A4 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 25.5 | 4.5 | 30 | 25.5 | 4.5 |  |  |  | 45 | 45 | 45 | 15 | 15 | 45 | 100% | 100% | 100% | 33.33% | 33.33% | 100% |  |  | DTC-RACK-R3-Z4E-R2-08 | 42.5 | 0 | 0 | 0 | 1 | 1 | 0
ZONE-R3-Z4E | ROW-R3-Z4E-R2 | 45 |  |  | LL-R3-E | AIRZONE-R3-E1 | RACK-R3-Z4E-R2-09 | POD-06 | RACKPDU-RACK-R3-Z4E-R2-09-A | RACKPDU-RACK-R3-Z4E-R2-09-B | 45 | 38.25 | 6.75 | 54 | 85% | 15% | RPP-R3-A4 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 25.5 | 4.5 | 30 | 25.5 | 4.5 |  |  |  | 45 | 45 | 45 | 15 | 15 | 45 | 100% | 100% | 100% | 33.33% | 33.33% | 100% |  |  | DTC-RACK-R3-Z4E-R2-09 | 42.5 | 0 | 0 | 0 | 1 | 1 | 0
ZONE-R3-Z4E | ROW-R3-Z4E-R2 | 45 |  |  | LL-R3-E | AIRZONE-R3-E1 | RACK-R3-Z4E-R2-10 | POD-06 | RACKPDU-RACK-R3-Z4E-R2-10-A | RACKPDU-RACK-R3-Z4E-R2-10-B | 45 | 38.25 | 6.75 | 54 | 85% | 15% | RPP-R3-A4 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 25.5 | 4.5 | 30 | 25.5 | 4.5 |  |  |  | 45 | 45 | 45 | 15 | 15 | 45 | 100% | 100% | 100% | 33.33% | 33.33% | 100% |  |  | DTC-RACK-R3-Z4E-R2-10 | 42.5 | 0 | 0 | 0 | 1 | 1 | 0
ZONE-R3-Z4E | ROW-R3-Z4E-R2 | 45 |  |  | LL-R3-E | AIRZONE-R3-E1 | RACK-R3-Z4E-R2-11 | POD-06 | RACKPDU-RACK-R3-Z4E-R2-11-A | RACKPDU-RACK-R3-Z4E-R2-11-B | 45 | 38.25 | 6.75 | 54 | 85% | 15% | RPP-R3-A4 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 25.5 | 4.5 | 30 | 25.5 | 4.5 |  |  |  | 45 | 45 | 45 | 15 | 15 | 45 | 100% | 100% | 100% | 33.33% | 33.33% | 100% |  |  | DTC-RACK-R3-Z4E-R2-11 | 42.5 | 0 | 0 | 0 | 1 | 1 | 0
ZONE-R3-Z4E | ROW-R3-Z4E-R2 | 45 |  |  | LL-R3-E | AIRZONE-R3-E1 | RACK-R3-Z4E-R2-12 | POD-06 | RACKPDU-RACK-R3-Z4E-R2-12-A | RACKPDU-RACK-R3-Z4E-R2-12-B | 45 | 38.25 | 6.75 | 54 | 85% | 15% | RPP-R3-A4 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 25.5 | 4.5 | 30 | 25.5 | 4.5 |  |  |  | 45 | 45 | 45 | 15 | 15 | 45 | 100% | 100% | 100% | 33.33% | 33.33% | 100% |  |  | DTC-RACK-R3-Z4E-R2-12 | 42.5 | 0 | 0 | 0 | 1 | 1 | 0
ZONE-R3-Z5E | ROW-R3-Z5E-R1 | 45 |  |  | LL-R3-E | AIRZONE-R3-E1 | RACK-R3-Z5E-R1-01 | POD-06 | RACKPDU-RACK-R3-Z5E-R1-01-A | RACKPDU-RACK-R3-Z5E-R1-01-B | 45 | 38.25 | 6.75 | 54 | 85% | 15% | RPP-R3-A3 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 25.5 | 4.5 | 30 | 25.5 | 4.5 |  |  |  | 45 | 45 | 45 | 15 | 15 | 45 | 100% | 100% | 100% | 33.33% | 33.33% | 100% |  |  | DTC-RACK-R3-Z5E-R1-01 | 42.5 | 0 | 0 | 0 | 1 | 1 | 0
ZONE-R3-Z5E | ROW-R3-Z5E-R1 | 45 |  |  | LL-R3-E | AIRZONE-R3-E1 | RACK-R3-Z5E-R1-02 | POD-06 | RACKPDU-RACK-R3-Z5E-R1-02-A | RACKPDU-RACK-R3-Z5E-R1-02-B | 45 | 38.25 | 6.75 | 54 | 85% | 15% | RPP-R3-A4 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 25.5 | 4.5 | 30 | 25.5 | 4.5 |  |  |  | 45 | 45 | 45 | 15 | 15 | 45 | 100% | 100% | 100% | 33.33% | 33.33% | 100% |  |  | DTC-RACK-R3-Z5E-R1-02 | 42.5 | 0 | 0 | 0 | 1 | 1 | 0
ZONE-R3-Z5E | ROW-R3-Z5E-R1 | 45 |  |  | LL-R3-E | AIRZONE-R3-E1 | RACK-R3-Z5E-R1-03 | POD-06 | RACKPDU-RACK-R3-Z5E-R1-03-A | RACKPDU-RACK-R3-Z5E-R1-03-B | 45 | 38.25 | 6.75 | 54 | 85% | 15% | RPP-R3-A3 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 25.5 | 4.5 | 30 | 25.5 | 4.5 |  |  |  | 45 | 45 | 45 | 15 | 15 | 45 | 100% | 100% | 100% | 33.33% | 33.33% | 100% |  |  | DTC-RACK-R3-Z5E-R1-03 | 42.5 | 0 | 0 | 0 | 1 | 1 | 0
ZONE-R3-Z5E | ROW-R3-Z5E-R1 | 45 |  |  | LL-R3-E | AIRZONE-R3-E1 | RACK-R3-Z5E-R1-04 | POD-06 | RACKPDU-RACK-R3-Z5E-R1-04-A | RACKPDU-RACK-R3-Z5E-R1-04-B | 45 | 38.25 | 6.75 | 54 | 85% | 15% | RPP-R3-A4 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 25.5 | 4.5 | 30 | 25.5 | 4.5 |  |  |  | 45 | 45 | 45 | 15 | 15 | 45 | 100% | 100% | 100% | 33.33% | 33.33% | 100% |  |  | DTC-RACK-R3-Z5E-R1-04 | 42.5 | 0 | 0 | 0 | 1 | 1 | 0
ZONE-R3-Z5E | ROW-R3-Z5E-R1 | 45 |  |  | LL-R3-E | AIRZONE-R3-E1 | RACK-R3-Z5E-R1-05 | POD-06 | RACKPDU-RACK-R3-Z5E-R1-05-A | RACKPDU-RACK-R3-Z5E-R1-05-B | 45 | 38.25 | 6.75 | 54 | 85% | 15% | RPP-R3-A3 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 25.5 | 4.5 | 30 | 25.5 | 4.5 |  |  |  | 45 | 45 | 45 | 15 | 15 | 45 | 100% | 100% | 100% | 33.33% | 33.33% | 100% |  |  | DTC-RACK-R3-Z5E-R1-05 | 42.5 | 0 | 0 | 0 | 1 | 1 | 0
ZONE-R3-Z5E | ROW-R3-Z5E-R1 | 45 |  |  | LL-R3-E | AIRZONE-R3-E1 | RACK-R3-Z5E-R1-06 | POD-06 | RACKPDU-RACK-R3-Z5E-R1-06-A | RACKPDU-RACK-R3-Z5E-R1-06-B | 45 | 38.25 | 6.75 | 54 | 85% | 15% | RPP-R3-A4 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 25.5 | 4.5 | 30 | 25.5 | 4.5 |  |  |  | 45 | 45 | 45 | 15 | 15 | 45 | 100% | 100% | 100% | 33.33% | 33.33% | 100% |  |  | DTC-RACK-R3-Z5E-R1-06 | 42.5 | 0 | 0 | 0 | 1 | 1 | 0
ZONE-R3-Z5E | ROW-R3-Z5E-R1 | 45 |  |  | LL-R3-E | AIRZONE-R3-E1 | RACK-R3-Z5E-R1-07 | POD-06 | RACKPDU-RACK-R3-Z5E-R1-07-A | RACKPDU-RACK-R3-Z5E-R1-07-B | 45 | 38.25 | 6.75 | 54 | 85% | 15% | RPP-R3-A3 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 25.5 | 4.5 | 30 | 25.5 | 4.5 |  |  |  | 45 | 45 | 45 | 15 | 15 | 45 | 100% | 100% | 100% | 33.33% | 33.33% | 100% |  |  | DTC-RACK-R3-Z5E-R1-07 | 42.5 | 0 | 0 | 0 | 1 | 1 | 0
ZONE-R3-Z5E | ROW-R3-Z5E-R1 | 45 |  |  | LL-R3-E | AIRZONE-R3-E1 | RACK-R3-Z5E-R1-08 | POD-06 | RACKPDU-RACK-R3-Z5E-R1-08-A | RACKPDU-RACK-R3-Z5E-R1-08-B | 45 | 38.25 | 6.75 | 54 | 85% | 15% | RPP-R3-A4 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 25.5 | 4.5 | 30 | 25.5 | 4.5 |  |  |  | 45 | 45 | 45 | 15 | 15 | 45 | 100% | 100% | 100% | 33.33% | 33.33% | 100% |  |  | DTC-RACK-R3-Z5E-R1-08 | 42.5 | 0 | 0 | 0 | 1 | 1 | 0
ZONE-R3-Z5E | ROW-R3-Z5E-R1 | 45 |  |  | LL-R3-E | AIRZONE-R3-E1 | RACK-R3-Z5E-R1-09 | POD-06 | RACKPDU-RACK-R3-Z5E-R1-09-A | RACKPDU-RACK-R3-Z5E-R1-09-B | 45 | 38.25 | 6.75 | 54 | 85% | 15% | RPP-R3-A3 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 25.5 | 4.5 | 30 | 25.5 | 4.5 |  |  |  | 45 | 45 | 45 | 15 | 15 | 45 | 100% | 100% | 100% | 33.33% | 33.33% | 100% |  |  | DTC-RACK-R3-Z5E-R1-09 | 42.5 | 0 | 0 | 0 | 1 | 1 | 0
ZONE-R3-Z5E | ROW-R3-Z5E-R1 | 45 |  |  | LL-R3-E | AIRZONE-R3-E1 | RACK-R3-Z5E-R1-10 | POD-06 | RACKPDU-RACK-R3-Z5E-R1-10-A | RACKPDU-RACK-R3-Z5E-R1-10-B | 45 | 38.25 | 6.75 | 54 | 85% | 15% | RPP-R3-A4 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 25.5 | 4.5 | 30 | 25.5 | 4.5 |  |  |  | 45 | 45 | 45 | 15 | 15 | 45 | 100% | 100% | 100% | 33.33% | 33.33% | 100% |  |  | DTC-RACK-R3-Z5E-R1-10 | 42.5 | 0 | 0 | 0 | 1 | 1 | 0
ZONE-R3-Z5E | ROW-R3-Z5E-R1 | 45 |  |  | LL-R3-E | AIRZONE-R3-E1 | RACK-R3-Z5E-R1-11 | POD-06 | RACKPDU-RACK-R3-Z5E-R1-11-A | RACKPDU-RACK-R3-Z5E-R1-11-B | 45 | 38.25 | 6.75 | 54 | 85% | 15% | RPP-R3-A3 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 25.5 | 4.5 | 30 | 25.5 | 4.5 |  |  |  | 45 | 45 | 45 | 15 | 15 | 45 | 100% | 100% | 100% | 33.33% | 33.33% | 100% |  |  | DTC-RACK-R3-Z5E-R1-11 | 42.5 | 0 | 0 | 0 | 1 | 1 | 0
ZONE-R3-Z5E | ROW-R3-Z5E-R1 | 45 |  |  | LL-R3-E | AIRZONE-R3-E1 | RACK-R3-Z5E-R1-12 | POD-06 | RACKPDU-RACK-R3-Z5E-R1-12-A | RACKPDU-RACK-R3-Z5E-R1-12-B | 45 | 38.25 | 6.75 | 54 | 85% | 15% | RPP-R3-A4 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 25.5 | 4.5 | 30 | 25.5 | 4.5 |  |  |  | 45 | 45 | 45 | 15 | 15 | 45 | 100% | 100% | 100% | 33.33% | 33.33% | 100% |  |  | DTC-RACK-R3-Z5E-R1-12 | 42.5 | 0 | 0 | 0 | 1 | 1 | 0
ZONE-R3-Z5E | ROW-R3-Z5E-R2 | 45 |  |  | LL-R3-E | AIRZONE-R3-E1 | RACK-R3-Z5E-R2-01 | POD-06 | RACKPDU-RACK-R3-Z5E-R2-01-A | RACKPDU-RACK-R3-Z5E-R2-01-B | 45 | 38.25 | 6.75 | 54 | 85% | 15% | RPP-R3-A3 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 25.5 | 4.5 | [6 empty] | 45 | 45 | 45 | 15 | 45 | 45 | 100% | 100% | 100% | 33.33% | 100% | 100% |  |  | DTC-RACK-R3-Z5E-R2-01 | 42.5 | 0 | 0 | 0 | 1 | 0 | 0
ZONE-R3-Z5E | ROW-R3-Z5E-R2 | 45 |  |  | LL-R3-E | AIRZONE-R3-E1 | RACK-R3-Z5E-R2-02 | POD-06 | RACKPDU-RACK-R3-Z5E-R2-02-A | RACKPDU-RACK-R3-Z5E-R2-02-B | 45 | 38.25 | 6.75 | 54 | 85% | 15% | RPP-R3-A4 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 25.5 | 4.5 | [6 empty] | 45 | 45 | 45 | 15 | 45 | 45 | 100% | 100% | 100% | 33.33% | 100% | 100% |  |  | DTC-RACK-R3-Z5E-R2-02 | 42.5 | 0 | 0 | 0 | 1 | 0 | 0
ZONE-R3-Z5E | ROW-R3-Z5E-R2 | 45 |  |  | LL-R3-E | AIRZONE-R3-E1 | RACK-R3-Z5E-R2-03 | POD-06 | RACKPDU-RACK-R3-Z5E-R2-03-A | RACKPDU-RACK-R3-Z5E-R2-03-B | 45 | 38.25 | 6.75 | 54 | 85% | 15% | RPP-R3-A3 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 25.5 | 4.5 | [6 empty] | 45 | 45 | 45 | 15 | 45 | 45 | 100% | 100% | 100% | 33.33% | 100% | 100% |  |  | DTC-RACK-R3-Z5E-R2-03 | 42.5 | 0 | 0 | 0 | 1 | 0 | 0
ZONE-R3-Z5E | ROW-R3-Z5E-R2 | 45 |  |  | LL-R3-E | AIRZONE-R3-E1 | RACK-R3-Z5E-R2-04 | POD-06 | RACKPDU-RACK-R3-Z5E-R2-04-A | RACKPDU-RACK-R3-Z5E-R2-04-B | 45 | 38.25 | 6.75 | 54 | 85% | 15% | RPP-R3-A4 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 25.5 | 4.5 | [6 empty] | 45 | 45 | 45 | 15 | 45 | 45 | 100% | 100% | 100% | 33.33% | 100% | 100% |  |  | DTC-RACK-R3-Z5E-R2-04 | 42.5 | 0 | 0 | 0 | 1 | 0 | 0
ZONE-R3-Z5E | ROW-R3-Z5E-R2 | 45 |  |  | LL-R3-E | AIRZONE-R3-E1 | RACK-R3-Z5E-R2-05 | POD-06 | RACKPDU-RACK-R3-Z5E-R2-05-A | RACKPDU-RACK-R3-Z5E-R2-05-B | 45 | 38.25 | 6.75 | 54 | 85% | 15% | RPP-R3-A3 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 25.5 | 4.5 |  | 0 | 0 |  |  |  | 45 | 45 | 45 | 15 | 45 | 45 | 100% | 100% | 100% | 33.33% | 100% | 100% |  |  | DTC-RACK-R3-Z5E-R2-05 | 42.5 | 0 | 0 | 0 | 1 | 0 | 0
ZONE-R3-Z5E | ROW-R3-Z5E-R2 | 45 |  |  | LL-R3-E | AIRZONE-R3-E1 | RACK-R3-Z5E-R2-06 | POD-06 | RACKPDU-RACK-R3-Z5E-R2-06-A | RACKPDU-RACK-R3-Z5E-R2-06-B | 45 | 38.25 | 6.75 | 54 | 85% | 15% | RPP-R3-A4 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 25.5 | 4.5 |  | 0 | 0 |  |  |  | 45 | 45 | 45 | 15 | 45 | 45 | 100% | 100% | 100% | 33.33% | 100% | 100% |  |  | DTC-RACK-R3-Z5E-R2-06 | 42.5 | 0 | 0 | 0 | 1 | 0 | 0
ZONE-R3-Z5E | ROW-R3-Z5E-R2 | 45 |  |  | LL-R3-E | AIRZONE-R3-E1 | RACK-R3-Z5E-R2-07 | POD-06 | RACKPDU-RACK-R3-Z5E-R2-07-A | RACKPDU-RACK-R3-Z5E-R2-07-B | 45 | 38.25 | 6.75 | 54 | 85% | 15% | RPP-R3-A3 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 25.5 | 4.5 |  | 0 | 0 |  |  |  | 45 | 45 | 45 | 15 | 45 | 45 | 100% | 100% | 100% | 33.33% | 100% | 100% |  |  | DTC-RACK-R3-Z5E-R2-07 | 42.5 | 0 | 0 | 0 | 1 | 0 | 0
ZONE-R3-Z5E | ROW-R3-Z5E-R2 | 45 |  |  | LL-R3-E | AIRZONE-R3-E1 | RACK-R3-Z5E-R2-08 | POD-06 | RACKPDU-RACK-R3-Z5E-R2-08-A | RACKPDU-RACK-R3-Z5E-R2-08-B | 45 | 38.25 | 6.75 | 54 | 85% | 15% | RPP-R3-A4 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 25.5 | 4.5 |  | 0 | 0 |  |  |  | 45 | 45 | 45 | 15 | 45 | 45 | 100% | 100% | 100% | 33.33% | 100% | 100% |  |  | DTC-RACK-R3-Z5E-R2-08 | 42.5 | 0 | 0 | 0 | 1 | 0 | 0
ZONE-R3-Z5E | ROW-R3-Z5E-R2 | 45 |  |  | LL-R3-E | AIRZONE-R3-E1 | RACK-R3-Z5E-R2-09 | POD-06 | RACKPDU-RACK-R3-Z5E-R2-09-A | RACKPDU-RACK-R3-Z5E-R2-09-B | 45 | 38.25 | 6.75 | 54 | 85% | 15% | RPP-R3-A3 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 25.5 | 4.5 |  | 0 | 0 |  |  |  | 45 | 45 | 45 | 15 | 45 | 45 | 100% | 100% | 100% | 33.33% | 100% | 100% |  |  | DTC-RACK-R3-Z5E-R2-09 | 42.5 | 0 | 0 | 0 | 1 | 0 | 0
ZONE-R3-Z5E | ROW-R3-Z5E-R2 | 45 |  |  | LL-R3-E | AIRZONE-R3-E1 | RACK-R3-Z5E-R2-10 | POD-06 | RACKPDU-RACK-R3-Z5E-R2-10-A | RACKPDU-RACK-R3-Z5E-R2-10-B | 45 | 38.25 | 6.75 | 54 | 85% | 15% | RPP-R3-A4 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 25.5 | 4.5 |  | 0 | 0 |  |  |  | 45 | 45 | 45 | 15 | 45 | 45 | 100% | 100% | 100% | 33.33% | 100% | 100% |  |  | DTC-RACK-R3-Z5E-R2-10 | 42.5 | 0 | 0 | 0 | 1 | 0 | 0
ZONE-R3-Z5E | ROW-R3-Z5E-R2 | 45 |  |  | LL-R3-E | AIRZONE-R3-E1 | RACK-R3-Z5E-R2-11 | POD-06 | RACKPDU-RACK-R3-Z5E-R2-11-A | RACKPDU-RACK-R3-Z5E-R2-11-B | 45 | 38.25 | 6.75 | 54 | 85% | 15% | RPP-R3-A3 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 25.5 | 4.5 |  | 0 | 0 |  |  |  | 45 | 45 | 45 | 15 | 45 | 45 | 100% | 100% | 100% | 33.33% | 100% | 100% |  |  | DTC-RACK-R3-Z5E-R2-11 | 42.5 | 0 | 0 | 0 | 1 | 0 | 0
ZONE-R3-Z5E | ROW-R3-Z5E-R2 | 45 |  |  | LL-R3-E | AIRZONE-R3-E1 | RACK-R3-Z5E-R2-12 | POD-06 | RACKPDU-RACK-R3-Z5E-R2-12-A | RACKPDU-RACK-R3-Z5E-R2-12-B | 45 | 38.25 | 6.75 | 54 | 85% | 15% | RPP-R3-A4 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 25.5 | 4.5 |  | 0 | 0 |  |  |  | 45 | 45 | 45 | 15 | 45 | 45 | 100% | 100% | 100% | 33.33% | 100% | 100% |  |  | DTC-RACK-R3-Z5E-R2-12 | 42.5 | 0 | 0 | 0 | 1 | 0 | 0
ZONE-R3-Z6E | ROW-R3-Z6E-R1 | 45 |  |  | LL-R3-E | AIRZONE-R3-E2 | RACK-R3-Z6E-R1-01 | POD-06 | RACKPDU-RACK-R3-Z6E-R1-01-A | RACKPDU-RACK-R3-Z6E-R1-01-B | 45 | 38.25 | 6.75 | 54 | 85% | 15% | RPP-R3-A3 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 25.5 | 4.5 | 30 | 25.5 | 4.5 |  |  |  | 45 | 45 | 45 | 15 | 15 | 45 | 100% | 100% | 100% | 33.33% | 33.33% | 100% |  |  | DTC-RACK-R3-Z6E-R1-01 | 42.5 | 0 | 0 | 0 | 1 | 1 | 0
ZONE-R3-Z6E | ROW-R3-Z6E-R1 | 45 |  |  | LL-R3-E | AIRZONE-R3-E2 | RACK-R3-Z6E-R1-02 | POD-06 | RACKPDU-RACK-R3-Z6E-R1-02-A | RACKPDU-RACK-R3-Z6E-R1-02-B | 45 | 38.25 | 6.75 | 54 | 85% | 15% | RPP-R3-A4 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 25.5 | 4.5 | 30 | 25.5 | 4.5 |  |  |  | 45 | 45 | 45 | 15 | 15 | 45 | 100% | 100% | 100% | 33.33% | 33.33% | 100% |  |  | DTC-RACK-R3-Z6E-R1-02 | 42.5 | 0 | 0 | 0 | 1 | 1 | 0
ZONE-R3-Z6E | ROW-R3-Z6E-R1 | 45 |  |  | LL-R3-E | AIRZONE-R3-E2 | RACK-R3-Z6E-R1-03 | POD-06 | RACKPDU-RACK-R3-Z6E-R1-03-A | RACKPDU-RACK-R3-Z6E-R1-03-B | 45 | 38.25 | 6.75 | 54 | 85% | 15% | RPP-R3-A3 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 25.5 | 4.5 | 30 | 25.5 | 4.5 |  |  |  | 45 | 45 | 45 | 15 | 15 | 45 | 100% | 100% | 100% | 33.33% | 33.33% | 100% |  |  | DTC-RACK-R3-Z6E-R1-03 | 42.5 | 0 | 0 | 0 | 1 | 1 | 0
ZONE-R3-Z6E | ROW-R3-Z6E-R1 | 45 |  |  | LL-R3-E | AIRZONE-R3-E2 | RACK-R3-Z6E-R1-04 | POD-06 | RACKPDU-RACK-R3-Z6E-R1-04-A | RACKPDU-RACK-R3-Z6E-R1-04-B | 45 | 38.25 | 6.75 | 54 | 85% | 15% | RPP-R3-A4 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 25.5 | 4.5 | 30 | 25.5 | 4.5 |  |  |  | 45 | 45 | 45 | 15 | 15 | 45 | 100% | 100% | 100% | 33.33% | 33.33% | 100% |  |  | DTC-RACK-R3-Z6E-R1-04 | 42.5 | 0 | 0 | 0 | 1 | 1 | 0
ZONE-R3-Z6E | ROW-R3-Z6E-R1 | 45 |  |  | LL-R3-E | AIRZONE-R3-E2 | RACK-R3-Z6E-R1-05 | POD-06 | RACKPDU-RACK-R3-Z6E-R1-05-A | RACKPDU-RACK-R3-Z6E-R1-05-B | 45 | 38.25 | 6.75 | 54 | 85% | 15% | RPP-R3-A3 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 25.5 | 4.5 | 30 | 25.5 | 4.5 |  |  |  | 45 | 45 | 45 | 15 | 15 | 45 | 100% | 100% | 100% | 33.33% | 33.33% | 100% |  |  | DTC-RACK-R3-Z6E-R1-05 | 42.5 | 0 | 0 | 0 | 1 | 1 | 0
ZONE-R3-Z6E | ROW-R3-Z6E-R1 | 45 |  |  | LL-R3-E | AIRZONE-R3-E2 | RACK-R3-Z6E-R1-06 | POD-06 | RACKPDU-RACK-R3-Z6E-R1-06-A | RACKPDU-RACK-R3-Z6E-R1-06-B | 45 | 38.25 | 6.75 | 54 | 85% | 15% | RPP-R3-A4 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 25.5 | 4.5 | 30 | 25.5 | 4.5 |  |  |  | 45 | 45 | 45 | 15 | 15 | 45 | 100% | 100% | 100% | 33.33% | 33.33% | 100% |  |  | DTC-RACK-R3-Z6E-R1-06 | 42.5 | 0 | 0 | 0 | 1 | 1 | 0
ZONE-R3-Z6E | ROW-R3-Z6E-R1 | 45 |  |  | LL-R3-E | AIRZONE-R3-E2 | RACK-R3-Z6E-R1-07 | POD-06 | RACKPDU-RACK-R3-Z6E-R1-07-A | RACKPDU-RACK-R3-Z6E-R1-07-B | 45 | 38.25 | 6.75 | 54 | 85% | 15% | RPP-R3-A3 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 25.5 | 4.5 | 30 | 25.5 | 4.5 |  |  |  | 45 | 45 | 45 | 15 | 15 | 45 | 100% | 100% | 100% | 33.33% | 33.33% | 100% |  |  | DTC-RACK-R3-Z6E-R1-07 | 42.5 | 0 | 0 | 0 | 1 | 1 | 0
ZONE-R3-Z6E | ROW-R3-Z6E-R1 | 45 |  |  | LL-R3-E | AIRZONE-R3-E2 | RACK-R3-Z6E-R1-08 | POD-06 | RACKPDU-RACK-R3-Z6E-R1-08-A | RACKPDU-RACK-R3-Z6E-R1-08-B | 45 | 38.25 | 6.75 | 54 | 85% | 15% | RPP-R3-A4 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 25.5 | 4.5 | 30 | 25.5 | 4.5 |  |  |  | 45 | 45 | 45 | 15 | 15 | 45 | 100% | 100% | 100% | 33.33% | 33.33% | 100% |  |  | DTC-RACK-R3-Z6E-R1-08 | 42.5 | 0 | 0 | 0 | 1 | 1 | 0
ZONE-R3-Z6E | ROW-R3-Z6E-R1 | 45 |  |  | LL-R3-E | AIRZONE-R3-E2 | RACK-R3-Z6E-R1-09 | POD-06 | RACKPDU-RACK-R3-Z6E-R1-09-A | RACKPDU-RACK-R3-Z6E-R1-09-B | 45 | 38.25 | 6.75 | 54 | 85% | 15% | RPP-R3-A3 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 25.5 | 4.5 | 30 | 25.5 | 4.5 |  |  |  | 45 | 45 | 45 | 15 | 15 | 45 | 100% | 100% | 100% | 33.33% | 33.33% | 100% |  |  | DTC-RACK-R3-Z6E-R1-09 | 42.5 | 0 | 0 | 0 | 1 | 1 | 0
ZONE-R3-Z6E | ROW-R3-Z6E-R1 | 45 |  |  | LL-R3-E | AIRZONE-R3-E2 | RACK-R3-Z6E-R1-10 | POD-06 | RACKPDU-RACK-R3-Z6E-R1-10-A | RACKPDU-RACK-R3-Z6E-R1-10-B | 45 | 38.25 | 6.75 | 54 | 85% | 15% | RPP-R3-A4 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 25.5 | 4.5 | 30 | 25.5 | 4.5 |  |  |  | 45 | 45 | 45 | 15 | 15 | 45 | 100% | 100% | 100% | 33.33% | 33.33% | 100% |  |  | DTC-RACK-R3-Z6E-R1-10 | 42.5 | 0 | 0 | 0 | 1 | 1 | 0
ZONE-R3-Z6E | ROW-R3-Z6E-R1 | 45 |  |  | LL-R3-E | AIRZONE-R3-E2 | RACK-R3-Z6E-R1-11 | POD-06 | RACKPDU-RACK-R3-Z6E-R1-11-A | RACKPDU-RACK-R3-Z6E-R1-11-B | 45 | 38.25 | 6.75 | 54 | 85% | 15% | RPP-R3-A3 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 25.5 | 4.5 | 30 | 25.5 | 4.5 |  |  |  | 45 | 45 | 45 | 15 | 15 | 45 | 100% | 100% | 100% | 33.33% | 33.33% | 100% |  |  | DTC-RACK-R3-Z6E-R1-11 | 42.5 | 0 | 0 | 0 | 1 | 1 | 0
ZONE-R3-Z6E | ROW-R3-Z6E-R1 | 45 |  |  | LL-R3-E | AIRZONE-R3-E2 | RACK-R3-Z6E-R1-12 | POD-06 | RACKPDU-RACK-R3-Z6E-R1-12-A | RACKPDU-RACK-R3-Z6E-R1-12-B | 45 | 38.25 | 6.75 | 54 | 85% | 15% | RPP-R3-A4 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 25.5 | 4.5 | 30 | 25.5 | 4.5 |  |  |  | 45 | 45 | 45 | 15 | 15 | 45 | 100% | 100% | 100% | 33.33% | 33.33% | 100% |  |  | DTC-RACK-R3-Z6E-R1-12 | 42.5 | 0 | 0 | 0 | 1 | 1 | 0
ZONE-R3-Z6E | ROW-R3-Z6E-R2 | 45 |  |  | LL-R3-E | AIRZONE-R3-E2 | RACK-R3-Z6E-R2-01 | POD-06 | RACKPDU-RACK-R3-Z6E-R2-01-A | RACKPDU-RACK-R3-Z6E-R2-01-B | 45 | 38.25 | 6.75 | 54 | 85% | 15% | RPP-R3-A3 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 30 | 25.5 | 4.5 |  |  |  | 45 | 45 | 45 | 45 | 15 | 45 | 100% | 100% | 100% | 100% | 33.33% | 100% |  |  | DTC-RACK-R3-Z6E-R2-01 | 42.5 | 0 | 0 | 0 | 0 | 1 | 0
ZONE-R3-Z6E | ROW-R3-Z6E-R2 | 45 |  |  | LL-R3-E | AIRZONE-R3-E2 | RACK-R3-Z6E-R2-02 | POD-06 | RACKPDU-RACK-R3-Z6E-R2-02-A | RACKPDU-RACK-R3-Z6E-R2-02-B | 45 | 38.25 | 6.75 | 54 | 85% | 15% | RPP-R3-A4 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 30 | 25.5 | 4.5 |  |  |  | 45 | 45 | 45 | 45 | 15 | 45 | 100% | 100% | 100% | 100% | 33.33% | 100% |  |  | DTC-RACK-R3-Z6E-R2-02 | 42.5 | 0 | 0 | 0 | 0 | 1 | 0
ZONE-R3-Z6E | ROW-R3-Z6E-R2 | 45 |  |  | LL-R3-E | AIRZONE-R3-E2 | RACK-R3-Z6E-R2-03 | POD-06 | RACKPDU-RACK-R3-Z6E-R2-03-A | RACKPDU-RACK-R3-Z6E-R2-03-B | 45 | 38.25 | 6.75 | 54 | 85% | 15% | RPP-R3-A3 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 30 | 25.5 | 4.5 |  |  |  | 45 | 45 | 45 | 45 | 15 | 45 | 100% | 100% | 100% | 100% | 33.33% | 100% |  |  | DTC-RACK-R3-Z6E-R2-03 | 42.5 | 0 | 0 | 0 | 0 | 1 | 0
ZONE-R3-Z6E | ROW-R3-Z6E-R2 | 45 |  |  | LL-R3-E | AIRZONE-R3-E2 | RACK-R3-Z6E-R2-04 | POD-06 | RACKPDU-RACK-R3-Z6E-R2-04-A | RACKPDU-RACK-R3-Z6E-R2-04-B | 45 | 38.25 | 6.75 | 54 | 85% | 15% | RPP-R3-A4 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 30 | 25.5 | 4.5 |  |  |  | 45 | 45 | 45 | 45 | 15 | 45 | 100% | 100% | 100% | 100% | 33.33% | 100% |  |  | DTC-RACK-R3-Z6E-R2-04 | 42.5 | 0 | 0 | 0 | 0 | 1 | 0
ZONE-R3-Z6E | ROW-R3-Z6E-R2 | 45 |  |  | LL-R3-E | AIRZONE-R3-E2 | RACK-R3-Z6E-R2-05 | POD-06 | RACKPDU-RACK-R3-Z6E-R2-05-A | RACKPDU-RACK-R3-Z6E-R2-05-B | 45 | 38.25 | 6.75 | 54 | 85% | 15% | RPP-R3-A3 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [6 empty] | 45 | 45 | 45 | 45 | 45 | 45 | 100% | 100% | 100% | 100% | 100% | 100% |  |  | DTC-RACK-R3-Z6E-R2-05 | 42.5 | 0 | 0 | 0 | 0 | 0 | 0
ZONE-R3-Z6E | ROW-R3-Z6E-R2 | 45 |  |  | LL-R3-E | AIRZONE-R3-E2 | RACK-R3-Z6E-R2-06 | POD-06 | RACKPDU-RACK-R3-Z6E-R2-06-A | RACKPDU-RACK-R3-Z6E-R2-06-B | 45 | 38.25 | 6.75 | 54 | 85% | 15% | RPP-R3-A4 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [6 empty] | 45 | 45 | 45 | 45 | 45 | 45 | 100% | 100% | 100% | 100% | 100% | 100% |  |  | DTC-RACK-R3-Z6E-R2-06 | 42.5 | 0 | 0 | 0 | 0 | 0 | 0
ZONE-R3-Z6E | ROW-R3-Z6E-R2 | 45 |  |  | LL-R3-E | AIRZONE-R3-E2 | RACK-R3-Z6E-R2-07 | POD-06 | RACKPDU-RACK-R3-Z6E-R2-07-A | RACKPDU-RACK-R3-Z6E-R2-07-B | 45 | 38.25 | 6.75 | 54 | 85% | 15% | RPP-R3-A3 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [6 empty] | 45 | 45 | 45 | 45 | 45 | 45 | 100% | 100% | 100% | 100% | 100% | 100% |  |  | DTC-RACK-R3-Z6E-R2-07 | 42.5 | 0 | 0 | 0 | 0 | 0 | 0
ZONE-R3-Z6E | ROW-R3-Z6E-R2 | 45 |  |  | LL-R3-E | AIRZONE-R3-E2 | RACK-R3-Z6E-R2-08 | POD-06 | RACKPDU-RACK-R3-Z6E-R2-08-A | RACKPDU-RACK-R3-Z6E-R2-08-B | 45 | 38.25 | 6.75 | 54 | 85% | 15% | RPP-R3-A4 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [6 empty] | 45 | 45 | 45 | 45 | 45 | 45 | 100% | 100% | 100% | 100% | 100% | 100% |  |  | DTC-RACK-R3-Z6E-R2-08 | 42.5 | 0 | 0 | 0 | 0 | 0 | 0
ZONE-R3-Z6E | ROW-R3-Z6E-R2 | 45 |  |  | LL-R3-E | AIRZONE-R3-E2 | RACK-R3-Z6E-R2-09 | POD-06 | RACKPDU-RACK-R3-Z6E-R2-09-A | RACKPDU-RACK-R3-Z6E-R2-09-B | 45 | 38.25 | 6.75 | 54 | 85% | 15% | RPP-R3-A3 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [6 empty] | 45 | 45 | 45 | 45 | 45 | 45 | 100% | 100% | 100% | 100% | 100% | 100% |  |  | DTC-RACK-R3-Z6E-R2-09 | 42.5 | 0 | 0 | 0 | 0 | 0 | 0
ZONE-R3-Z6E | ROW-R3-Z6E-R2 | 45 |  |  | LL-R3-E | AIRZONE-R3-E2 | RACK-R3-Z6E-R2-10 | POD-06 | RACKPDU-RACK-R3-Z6E-R2-10-A | RACKPDU-RACK-R3-Z6E-R2-10-B | 45 | 38.25 | 6.75 | 54 | 85% | 15% | RPP-R3-A4 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [6 empty] | 45 | 45 | 45 | 45 | 45 | 45 | 100% | 100% | 100% | 100% | 100% | 100% |  |  | DTC-RACK-R3-Z6E-R2-10 | 42.5 | 0 | 0 | 0 | 0 | 0 | 0
ZONE-R3-Z6E | ROW-R3-Z6E-R2 | 45 |  |  | LL-R3-E | AIRZONE-R3-E2 | RACK-R3-Z6E-R2-11 | POD-06 | RACKPDU-RACK-R3-Z6E-R2-11-A | RACKPDU-RACK-R3-Z6E-R2-11-B | 45 | 38.25 | 6.75 | 54 | 85% | 15% | RPP-R3-A3 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [6 empty] | 45 | 45 | 45 | 45 | 45 | 45 | 100% | 100% | 100% | 100% | 100% | 100% |  |  | DTC-RACK-R3-Z6E-R2-11 | 42.5 | 0 | 0 | 0 | 0 | 0 | 0
ZONE-R3-Z6E | ROW-R3-Z6E-R2 | 45 |  |  | LL-R3-E | AIRZONE-R3-E2 | RACK-R3-Z6E-R2-12 | POD-06 | RACKPDU-RACK-R3-Z6E-R2-12-A | RACKPDU-RACK-R3-Z6E-R2-12-B | 45 | 38.25 | 6.75 | 54 | 85% | 15% | RPP-R3-A4 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [6 empty] | 45 | 45 | 45 | 45 | 45 | 45 | 100% | 100% | 100% | 100% | 100% | 100% |  |  | DTC-RACK-R3-Z6E-R2-12 | 42.5 | 0 | 0 | 0 | 0 | 0 | 0
ZONE-R4-Z1 | ROW-R4-Z1-R1 | 20 |  |  | LL-R4 | AIRZONE-R4 | RACK-R4-Z1-R1-01 | POD-07 | RACKPDU-RACK-R4-Z1-R1-01-A | RACKPDU-RACK-R4-Z1-R1-01-B | 20 | 14 | 6 | 25 | 70% | 30% | RPP-R4-A5 | RPP-R4-B5 | RPDU-R4-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R4 | BDL-R4 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [6 empty] | 20 | 20 | 20 | 20 | 20 | 20 | 100% | 100% | 100% | 100% | 100% | 100% |  |  | DTC-RACK-R4-Z1-R1-01 | 15.5556 | 0 | 0 | 0 | 0 | 0 | 0
ZONE-R4-Z1 | ROW-R4-Z1-R1 | 20 |  |  | LL-R4 | AIRZONE-R4 | RACK-R4-Z1-R1-02 | POD-07 | RACKPDU-RACK-R4-Z1-R1-02-A | RACKPDU-RACK-R4-Z1-R1-02-B | 20 | 14 | 6 | 25 | 70% | 30% | RPP-R4-A6 | RPP-R4-B6 | RPDU-R4-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R4 | BDL-R4 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [6 empty] | 20 | 20 | 20 | 20 | 20 | 20 | 100% | 100% | 100% | 100% | 100% | 100% |  |  | DTC-RACK-R4-Z1-R1-02 | 15.5556 | 0 | 0 | 0 | 0 | 0 | 0
ZONE-R4-Z1 | ROW-R4-Z1-R1 | 20 |  |  | LL-R4 | AIRZONE-R4 | RACK-R4-Z1-R1-03 | POD-07 | RACKPDU-RACK-R4-Z1-R1-03-A | RACKPDU-RACK-R4-Z1-R1-03-B | 20 | 14 | 6 | 25 | 70% | 30% | RPP-R4-A5 | RPP-R4-B5 | RPDU-R4-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R4 | BDL-R4 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [6 empty] | 20 | 20 | 20 | 20 | 20 | 20 | 100% | 100% | 100% | 100% | 100% | 100% |  |  | DTC-RACK-R4-Z1-R1-03 | 15.5556 | 0 | 0 | 0 | 0 | 0 | 0
ZONE-R4-Z1 | ROW-R4-Z1-R1 | 20 |  |  | LL-R4 | AIRZONE-R4 | RACK-R4-Z1-R1-04 | POD-07 | RACKPDU-RACK-R4-Z1-R1-04-A | RACKPDU-RACK-R4-Z1-R1-04-B | 20 | 14 | 6 | 25 | 70% | 30% | RPP-R4-A6 | RPP-R4-B6 | RPDU-R4-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R4 | BDL-R4 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [6 empty] | 20 | 20 | 20 | 20 | 20 | 20 | 100% | 100% | 100% | 100% | 100% | 100% |  |  | DTC-RACK-R4-Z1-R1-04 | 15.5556 | 0 | 0 | 0 | 0 | 0 | 0
ZONE-R4-Z1 | ROW-R4-Z1-R1 | 20 |  |  | LL-R4 | AIRZONE-R4 | RACK-R4-Z1-R1-05 | POD-07 | RACKPDU-RACK-R4-Z1-R1-05-A | RACKPDU-RACK-R4-Z1-R1-05-B | 20 | 14 | 6 | 25 | 70% | 30% | RPP-R4-A5 | RPP-R4-B5 | RPDU-R4-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R4 | BDL-R4 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [6 empty] | 20 | 20 | 20 | 20 | 20 | 20 | 100% | 100% | 100% | 100% | 100% | 100% |  |  | DTC-RACK-R4-Z1-R1-05 | 15.5556 | 0 | 0 | 0 | 0 | 0 | 0
ZONE-R4-Z1 | ROW-R4-Z1-R1 | 20 |  |  | LL-R4 | AIRZONE-R4 | RACK-R4-Z1-R1-06 | POD-07 | RACKPDU-RACK-R4-Z1-R1-06-A | RACKPDU-RACK-R4-Z1-R1-06-B | 20 | 14 | 6 | 25 | 70% | 30% | RPP-R4-A6 | RPP-R4-B6 | RPDU-R4-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R4 | BDL-R4 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [6 empty] | 20 | 20 | 20 | 20 | 20 | 20 | 100% | 100% | 100% | 100% | 100% | 100% |  |  | DTC-RACK-R4-Z1-R1-06 | 15.5556 | 0 | 0 | 0 | 0 | 0 | 0
ZONE-R4-Z1 | ROW-R4-Z1-R1 | 20 |  |  | LL-R4 | AIRZONE-R4 | RACK-R4-Z1-R1-07 | POD-07 | RACKPDU-RACK-R4-Z1-R1-07-A | RACKPDU-RACK-R4-Z1-R1-07-B | 20 | 14 | 6 | 25 | 70% | 30% | RPP-R4-A5 | RPP-R4-B5 | RPDU-R4-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R4 | BDL-R4 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [6 empty] | 20 | 20 | 20 | 20 | 20 | 20 | 100% | 100% | 100% | 100% | 100% | 100% |  |  | DTC-RACK-R4-Z1-R1-07 | 15.5556 | 0 | 0 | 0 | 0 | 0 | 0
ZONE-R4-Z1 | ROW-R4-Z1-R1 | 20 |  |  | LL-R4 | AIRZONE-R4 | RACK-R4-Z1-R1-08 | POD-07 | RACKPDU-RACK-R4-Z1-R1-08-A | RACKPDU-RACK-R4-Z1-R1-08-B | 20 | 14 | 6 | 25 | 70% | 30% | RPP-R4-A6 | RPP-R4-B6 | RPDU-R4-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R4 | BDL-R4 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [6 empty] | 20 | 20 | 20 | 20 | 20 | 20 | 100% | 100% | 100% | 100% | 100% | 100% |  |  | DTC-RACK-R4-Z1-R1-08 | 15.5556 | 0 | 0 | 0 | 0 | 0 | 0
ZONE-R4-Z1 | ROW-R4-Z1-R1 | 20 |  |  | LL-R4 | AIRZONE-R4 | RACK-R4-Z1-R1-09 | POD-07 | RACKPDU-RACK-R4-Z1-R1-09-A | RACKPDU-RACK-R4-Z1-R1-09-B | 20 | 14 | 6 | 25 | 70% | 30% | RPP-R4-A5 | RPP-R4-B5 | RPDU-R4-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R4 | BDL-R4 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [6 empty] | 20 | 20 | 20 | 20 | 20 | 20 | 100% | 100% | 100% | 100% | 100% | 100% |  |  | DTC-RACK-R4-Z1-R1-09 | 15.5556 | 0 | 0 | 0 | 0 | 0 | 0
ZONE-R4-Z1 | ROW-R4-Z1-R1 | 20 |  |  | LL-R4 | AIRZONE-R4 | RACK-R4-Z1-R1-10 | POD-07 | RACKPDU-RACK-R4-Z1-R1-10-A | RACKPDU-RACK-R4-Z1-R1-10-B | 20 | 14 | 6 | 25 | 70% | 30% | RPP-R4-A6 | RPP-R4-B6 | RPDU-R4-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R4 | BDL-R4 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [6 empty] | 20 | 20 | 20 | 20 | 20 | 20 | 100% | 100% | 100% | 100% | 100% | 100% |  |  | DTC-RACK-R4-Z1-R1-10 | 15.5556 | 0 | 0 | 0 | 0 | 0 | 0
ZONE-R4-Z1 | ROW-R4-Z1-R1 | 20 |  |  | LL-R4 | AIRZONE-R4 | RACK-R4-Z1-R1-11 | POD-07 | RACKPDU-RACK-R4-Z1-R1-11-A | RACKPDU-RACK-R4-Z1-R1-11-B | 20 | 14 | 6 | 25 | 70% | 30% | RPP-R4-A5 | RPP-R4-B5 | RPDU-R4-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R4 | BDL-R4 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [6 empty] | 20 | 20 | 20 | 20 | 20 | 20 | 100% | 100% | 100% | 100% | 100% | 100% |  |  | DTC-RACK-R4-Z1-R1-11 | 15.5556 | 0 | 0 | 0 | 0 | 0 | 0
ZONE-R4-Z1 | ROW-R4-Z1-R1 | 20 |  |  | LL-R4 | AIRZONE-R4 | RACK-R4-Z1-R1-12 | POD-07 | RACKPDU-RACK-R4-Z1-R1-12-A | RACKPDU-RACK-R4-Z1-R1-12-B | 20 | 14 | 6 | 25 | 70% | 30% | RPP-R4-A6 | RPP-R4-B6 | RPDU-R4-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R4 | BDL-R4 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [6 empty] | 20 | 20 | 20 | 20 | 20 | 20 | 100% | 100% | 100% | 100% | 100% | 100% |  |  | DTC-RACK-R4-Z1-R1-12 | 15.5556 | 0 | 0 | 0 | 0 | 0 | 0
ZONE-R4-Z1 | ROW-R4-Z1-R2 | 20 |  |  | LL-R4 | AIRZONE-R4 | RACK-R4-Z1-R2-01 | POD-07 | RACKPDU-RACK-R4-Z1-R2-01-A | RACKPDU-RACK-R4-Z1-R2-01-B | 20 | 14 | 6 | 25 | 70% | 30% | RPP-R4-A5 | RPP-R4-B5 | RPDU-R4-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R4 | BDL-R4 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [6 empty] | 20 | 20 | 20 | 20 | 20 | 20 | 100% | 100% | 100% | 100% | 100% | 100% |  |  | DTC-RACK-R4-Z1-R2-01 | 15.5556 | 0 | 0 | 0 | 0 | 0 | 0
ZONE-R4-Z1 | ROW-R4-Z1-R2 | 20 |  |  | LL-R4 | AIRZONE-R4 | RACK-R4-Z1-R2-02 | POD-07 | RACKPDU-RACK-R4-Z1-R2-02-A | RACKPDU-RACK-R4-Z1-R2-02-B | 20 | 14 | 6 | 25 | 70% | 30% | RPP-R4-A6 | RPP-R4-B6 | RPDU-R4-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R4 | BDL-R4 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [6 empty] | 20 | 20 | 20 | 20 | 20 | 20 | 100% | 100% | 100% | 100% | 100% | 100% |  |  | DTC-RACK-R4-Z1-R2-02 | 15.5556 | 0 | 0 | 0 | 0 | 0 | 0
ZONE-R4-Z1 | ROW-R4-Z1-R2 | 20 |  |  | LL-R4 | AIRZONE-R4 | RACK-R4-Z1-R2-03 | POD-07 | RACKPDU-RACK-R4-Z1-R2-03-A | RACKPDU-RACK-R4-Z1-R2-03-B | 20 | 14 | 6 | 25 | 70% | 30% | RPP-R4-A5 | RPP-R4-B5 | RPDU-R4-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R4 | BDL-R4 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [6 empty] | 20 | 20 | 20 | 20 | 20 | 20 | 100% | 100% | 100% | 100% | 100% | 100% |  |  | DTC-RACK-R4-Z1-R2-03 | 15.5556 | 0 | 0 | 0 | 0 | 0 | 0
ZONE-R4-Z1 | ROW-R4-Z1-R2 | 20 |  |  | LL-R4 | AIRZONE-R4 | RACK-R4-Z1-R2-04 | POD-07 | RACKPDU-RACK-R4-Z1-R2-04-A | RACKPDU-RACK-R4-Z1-R2-04-B | 20 | 14 | 6 | 25 | 70% | 30% | RPP-R4-A6 | RPP-R4-B6 | RPDU-R4-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R4 | BDL-R4 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [6 empty] | 20 | 20 | 20 | 20 | 20 | 20 | 100% | 100% | 100% | 100% | 100% | 100% |  |  | DTC-RACK-R4-Z1-R2-04 | 15.5556 | 0 | 0 | 0 | 0 | 0 | 0
ZONE-R4-Z1 | ROW-R4-Z1-R2 | 20 |  |  | LL-R4 | AIRZONE-R4 | RACK-R4-Z1-R2-05 | POD-07 | RACKPDU-RACK-R4-Z1-R2-05-A | RACKPDU-RACK-R4-Z1-R2-05-B | 20 | 14 | 6 | 25 | 70% | 30% | RPP-R4-A5 | RPP-R4-B5 | RPDU-R4-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R4 | BDL-R4 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [6 empty] | 20 | 20 | 20 | 20 | 20 | 20 | 100% | 100% | 100% | 100% | 100% | 100% |  |  | DTC-RACK-R4-Z1-R2-05 | 15.5556 | 0 | 0 | 0 | 0 | 0 | 0
ZONE-R4-Z1 | ROW-R4-Z1-R2 | 20 |  |  | LL-R4 | AIRZONE-R4 | RACK-R4-Z1-R2-06 | POD-07 | RACKPDU-RACK-R4-Z1-R2-06-A | RACKPDU-RACK-R4-Z1-R2-06-B | 20 | 14 | 6 | 25 | 70% | 30% | RPP-R4-A6 | RPP-R4-B6 | RPDU-R4-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R4 | BDL-R4 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [6 empty] | 20 | 20 | 20 | 20 | 20 | 20 | 100% | 100% | 100% | 100% | 100% | 100% |  |  | DTC-RACK-R4-Z1-R2-06 | 15.5556 | 0 | 0 | 0 | 0 | 0 | 0
ZONE-R4-Z1 | ROW-R4-Z1-R2 | 20 |  |  | LL-R4 | AIRZONE-R4 | RACK-R4-Z1-R2-07 | POD-07 | RACKPDU-RACK-R4-Z1-R2-07-A | RACKPDU-RACK-R4-Z1-R2-07-B | 20 | 14 | 6 | 25 | 70% | 30% | RPP-R4-A5 | RPP-R4-B5 | RPDU-R4-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R4 | BDL-R4 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [6 empty] | 20 | 20 | 20 | 20 | 20 | 20 | 100% | 100% | 100% | 100% | 100% | 100% |  |  | DTC-RACK-R4-Z1-R2-07 | 15.5556 | 0 | 0 | 0 | 0 | 0 | 0
ZONE-R4-Z1 | ROW-R4-Z1-R2 | 20 |  |  | LL-R4 | AIRZONE-R4 | RACK-R4-Z1-R2-08 | POD-07 | RACKPDU-RACK-R4-Z1-R2-08-A | RACKPDU-RACK-R4-Z1-R2-08-B | 20 | 14 | 6 | 25 | 70% | 30% | RPP-R4-A6 | RPP-R4-B6 | RPDU-R4-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R4 | BDL-R4 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [6 empty] | 20 | 20 | 20 | 20 | 20 | 20 | 100% | 100% | 100% | 100% | 100% | 100% |  |  | DTC-RACK-R4-Z1-R2-08 | 15.5556 | 0 | 0 | 0 | 0 | 0 | 0
ZONE-R4-Z1 | ROW-R4-Z1-R2 | 20 |  |  | LL-R4 | AIRZONE-R4 | RACK-R4-Z1-R2-09 | POD-07 | RACKPDU-RACK-R4-Z1-R2-09-A | RACKPDU-RACK-R4-Z1-R2-09-B | 20 | 14 | 6 | 25 | 70% | 30% | RPP-R4-A5 | RPP-R4-B5 | RPDU-R4-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R4 | BDL-R4 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [6 empty] | 20 | 20 | 20 | 20 | 20 | 20 | 100% | 100% | 100% | 100% | 100% | 100% |  |  | DTC-RACK-R4-Z1-R2-09 | 15.5556 | 0 | 0 | 0 | 0 | 0 | 0
ZONE-R4-Z1 | ROW-R4-Z1-R2 | 20 |  |  | LL-R4 | AIRZONE-R4 | RACK-R4-Z1-R2-10 | POD-07 | RACKPDU-RACK-R4-Z1-R2-10-A | RACKPDU-RACK-R4-Z1-R2-10-B | 20 | 14 | 6 | 25 | 70% | 30% | RPP-R4-A6 | RPP-R4-B6 | RPDU-R4-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R4 | BDL-R4 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [6 empty] | 20 | 20 | 20 | 20 | 20 | 20 | 100% | 100% | 100% | 100% | 100% | 100% |  |  | DTC-RACK-R4-Z1-R2-10 | 15.5556 | 0 | 0 | 0 | 0 | 0 | 0
ZONE-R4-Z1 | ROW-R4-Z1-R2 | 20 |  |  | LL-R4 | AIRZONE-R4 | RACK-R4-Z1-R2-11 | POD-07 | RACKPDU-RACK-R4-Z1-R2-11-A | RACKPDU-RACK-R4-Z1-R2-11-B | 20 | 14 | 6 | 25 | 70% | 30% | RPP-R4-A5 | RPP-R4-B5 | RPDU-R4-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R4 | BDL-R4 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [6 empty] | 20 | 20 | 20 | 20 | 20 | 20 | 100% | 100% | 100% | 100% | 100% | 100% |  |  | DTC-RACK-R4-Z1-R2-11 | 15.5556 | 0 | 0 | 0 | 0 | 0 | 0
ZONE-R4-Z1 | ROW-R4-Z1-R2 | 20 |  |  | LL-R4 | AIRZONE-R4 | RACK-R4-Z1-R2-12 | POD-07 | RACKPDU-RACK-R4-Z1-R2-12-A | RACKPDU-RACK-R4-Z1-R2-12-B | 20 | 14 | 6 | 25 | 70% | 30% | RPP-R4-A6 | RPP-R4-B6 | RPDU-R4-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R4 | BDL-R4 | BDL-RPDU-R3R4 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [6 empty] | 20 | 20 | 20 | 20 | 20 | 20 | 100% | 100% | 100% | 100% | 100% | 100% |  |  | DTC-RACK-R4-Z1-R2-12 | 15.5556 | 0 | 0 | 0 | 0 | 0 | 0
ZONE-R5-Z1W | ROW-R5-Z1W-R1 | 60 |  |  | LL-R5-W | AIRZONE-R5-W | RACK-R5-Z1W-R1-01 | POD-08 | RACKPDU-RACK-R5-Z1W-R1-01-A | RACKPDU-RACK-R5-Z1W-R1-01-B | 60 | 51 | 9 | 72 | 85% | 15% | RPP-R5-A1 | RPP-R5-B1 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R5W | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [6 empty] | 60 | 60 | 60 | 60 | 60 | 60 | 100% | 100% | 100% | 100% | 100% | 100% |  |  | DTC-RACK-R5-Z1W-R1-01 | 56.6667 | 0 | 0 | 0 | 0 | 0 | 0
ZONE-R5-Z1W | ROW-R5-Z1W-R1 | 60 |  |  | LL-R5-W | AIRZONE-R5-W | RACK-R5-Z1W-R1-02 | POD-08 | RACKPDU-RACK-R5-Z1W-R1-02-A | RACKPDU-RACK-R5-Z1W-R1-02-B | 60 | 51 | 9 | 72 | 85% | 15% | RPP-R5-A1 | RPP-R5-B1 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R5W | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [6 empty] | 60 | 60 | 60 | 60 | 60 | 60 | 100% | 100% | 100% | 100% | 100% | 100% |  |  | DTC-RACK-R5-Z1W-R1-02 | 56.6667 | 0 | 0 | 0 | 0 | 0 | 0
ZONE-R5-Z1W | ROW-R5-Z1W-R1 | 60 |  |  | LL-R5-W | AIRZONE-R5-W | RACK-R5-Z1W-R1-03 | POD-08 | RACKPDU-RACK-R5-Z1W-R1-03-A | RACKPDU-RACK-R5-Z1W-R1-03-B | 60 | 51 | 9 | 72 | 85% | 15% | RPP-R5-A1 | RPP-R5-B1 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R5W | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [6 empty] | 60 | 60 | 60 | 60 | 60 | 60 | 100% | 100% | 100% | 100% | 100% | 100% |  |  | DTC-RACK-R5-Z1W-R1-03 | 56.6667 | 0 | 0 | 0 | 0 | 0 | 0
ZONE-R5-Z1W | ROW-R5-Z1W-R1 | 60 |  |  | LL-R5-W | AIRZONE-R5-W | RACK-R5-Z1W-R1-04 | POD-08 | RACKPDU-RACK-R5-Z1W-R1-04-A | RACKPDU-RACK-R5-Z1W-R1-04-B | 60 | 51 | 9 | 72 | 85% | 15% | RPP-R5-A1 | RPP-R5-B1 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R5W | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [6 empty] | 60 | 60 | 60 | 60 | 60 | 60 | 100% | 100% | 100% | 100% | 100% | 100% |  |  | DTC-RACK-R5-Z1W-R1-04 | 56.6667 | 0 | 0 | 0 | 0 | 0 | 0
ZONE-R5-Z1W | ROW-R5-Z1W-R1 | 60 |  |  | LL-R5-W | AIRZONE-R5-W | RACK-R5-Z1W-R1-05 | POD-08 | RACKPDU-RACK-R5-Z1W-R1-05-A | RACKPDU-RACK-R5-Z1W-R1-05-B | 60 | 51 | 9 | 72 | 85% | 15% | RPP-R5-A1 | RPP-R5-B1 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R5W | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [6 empty] | 60 | 60 | 60 | 60 | 60 | 60 | 100% | 100% | 100% | 100% | 100% | 100% |  |  | DTC-RACK-R5-Z1W-R1-05 | 56.6667 | 0 | 0 | 0 | 0 | 0 | 0
ZONE-R5-Z1W | ROW-R5-Z1W-R1 | 60 |  |  | LL-R5-W | AIRZONE-R5-W | RACK-R5-Z1W-R1-06 | POD-08 | RACKPDU-RACK-R5-Z1W-R1-06-A | RACKPDU-RACK-R5-Z1W-R1-06-B | 60 | 51 | 9 | 72 | 85% | 15% | RPP-R5-A1 | RPP-R5-B1 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R5W | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [6 empty] | 60 | 60 | 60 | 60 | 60 | 60 | 100% | 100% | 100% | 100% | 100% | 100% |  |  | DTC-RACK-R5-Z1W-R1-06 | 56.6667 | 0 | 0 | 0 | 0 | 0 | 0
ZONE-R5-Z1W | ROW-R5-Z1W-R1 | 60 |  |  | LL-R5-W | AIRZONE-R5-W | RACK-R5-Z1W-R1-07 | POD-08 | RACKPDU-RACK-R5-Z1W-R1-07-A | RACKPDU-RACK-R5-Z1W-R1-07-B | 60 | 51 | 9 | 72 | 85% | 15% | RPP-R5-A1 | RPP-R5-B1 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R5W | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [6 empty] | 60 | 60 | 60 | 60 | 60 | 60 | 100% | 100% | 100% | 100% | 100% | 100% |  |  | DTC-RACK-R5-Z1W-R1-07 | 56.6667 | 0 | 0 | 0 | 0 | 0 | 0
ZONE-R5-Z1W | ROW-R5-Z1W-R1 | 60 |  |  | LL-R5-W | AIRZONE-R5-W | RACK-R5-Z1W-R1-08 | POD-08 | RACKPDU-RACK-R5-Z1W-R1-08-A | RACKPDU-RACK-R5-Z1W-R1-08-B | 60 | 51 | 9 | 72 | 85% | 15% | RPP-R5-A1 | RPP-R5-B1 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R5W | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [6 empty] | 60 | 60 | 60 | 60 | 60 | 60 | 100% | 100% | 100% | 100% | 100% | 100% |  |  | DTC-RACK-R5-Z1W-R1-08 | 56.6667 | 0 | 0 | 0 | 0 | 0 | 0
ZONE-R5-Z1W | ROW-R5-Z1W-R1 | 60 |  |  | LL-R5-W | AIRZONE-R5-W | RACK-R5-Z1W-R1-09 | POD-08 | RACKPDU-RACK-R5-Z1W-R1-09-A | RACKPDU-RACK-R5-Z1W-R1-09-B | 60 | 51 | 9 | 72 | 85% | 15% | RPP-R5-A1 | RPP-R5-B1 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R5W | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [6 empty] | 60 | 60 | 60 | 60 | 60 | 60 | 100% | 100% | 100% | 100% | 100% | 100% |  |  | DTC-RACK-R5-Z1W-R1-09 | 56.6667 | 0 | 0 | 0 | 0 | 0 | 0
ZONE-R5-Z1W | ROW-R5-Z1W-R1 | 60 |  |  | LL-R5-W | AIRZONE-R5-W | RACK-R5-Z1W-R1-10 | POD-08 | RACKPDU-RACK-R5-Z1W-R1-10-A | RACKPDU-RACK-R5-Z1W-R1-10-B | 60 | 51 | 9 | 72 | 85% | 15% | RPP-R5-A1 | RPP-R5-B1 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R5W | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [6 empty] | 60 | 60 | 60 | 60 | 60 | 60 | 100% | 100% | 100% | 100% | 100% | 100% |  |  | DTC-RACK-R5-Z1W-R1-10 | 56.6667 | 0 | 0 | 0 | 0 | 0 | 0
ZONE-R5-Z1W | ROW-R5-Z1W-R1 | 60 |  |  | LL-R5-W | AIRZONE-R5-W | RACK-R5-Z1W-R1-11 | POD-08 | RACKPDU-RACK-R5-Z1W-R1-11-A | RACKPDU-RACK-R5-Z1W-R1-11-B | 60 | 51 | 9 | 72 | 85% | 15% | RPP-R5-A1 | RPP-R5-B1 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R5W | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [6 empty] | 60 | 60 | 60 | 60 | 60 | 60 | 100% | 100% | 100% | 100% | 100% | 100% |  |  | DTC-RACK-R5-Z1W-R1-11 | 56.6667 | 0 | 0 | 0 | 0 | 0 | 0
ZONE-R5-Z1W | ROW-R5-Z1W-R1 | 60 |  |  | LL-R5-W | AIRZONE-R5-W | RACK-R5-Z1W-R1-12 | POD-08 | RACKPDU-RACK-R5-Z1W-R1-12-A | RACKPDU-RACK-R5-Z1W-R1-12-B | 60 | 51 | 9 | 72 | 85% | 15% | RPP-R5-A1 | RPP-R5-B1 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R5W | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [6 empty] | 60 | 60 | 60 | 60 | 60 | 60 | 100% | 100% | 100% | 100% | 100% | 100% |  |  | DTC-RACK-R5-Z1W-R1-12 | 56.6667 | 0 | 0 | 0 | 0 | 0 | 0
ZONE-R5-Z1W | ROW-R5-Z1W-R2 | 60 |  |  | LL-R5-W | AIRZONE-R5-W | RACK-R5-Z1W-R2-01 | POD-08 | RACKPDU-RACK-R5-Z1W-R2-01-A | RACKPDU-RACK-R5-Z1W-R2-01-B | 60 | 51 | 9 | 72 | 85% | 15% | RPP-R5-A2 | RPP-R5-B2 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R5W | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [6 empty] | 60 | 60 | 60 | 60 | 60 | 60 | 100% | 100% | 100% | 100% | 100% | 100% |  |  | DTC-RACK-R5-Z1W-R2-01 | 56.6667 | 0 | 0 | 0 | 0 | 0 | 0
ZONE-R5-Z1W | ROW-R5-Z1W-R2 | 60 |  |  | LL-R5-W | AIRZONE-R5-W | RACK-R5-Z1W-R2-02 | POD-08 | RACKPDU-RACK-R5-Z1W-R2-02-A | RACKPDU-RACK-R5-Z1W-R2-02-B | 60 | 51 | 9 | 72 | 85% | 15% | RPP-R5-A2 | RPP-R5-B2 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R5W | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [6 empty] | 60 | 60 | 60 | 60 | 60 | 60 | 100% | 100% | 100% | 100% | 100% | 100% |  |  | DTC-RACK-R5-Z1W-R2-02 | 56.6667 | 0 | 0 | 0 | 0 | 0 | 0
ZONE-R5-Z1W | ROW-R5-Z1W-R2 | 60 |  |  | LL-R5-W | AIRZONE-R5-W | RACK-R5-Z1W-R2-03 | POD-08 | RACKPDU-RACK-R5-Z1W-R2-03-A | RACKPDU-RACK-R5-Z1W-R2-03-B | 60 | 51 | 9 | 72 | 85% | 15% | RPP-R5-A2 | RPP-R5-B2 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R5W | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [6 empty] | 60 | 60 | 60 | 60 | 60 | 60 | 100% | 100% | 100% | 100% | 100% | 100% |  |  | DTC-RACK-R5-Z1W-R2-03 | 56.6667 | 0 | 0 | 0 | 0 | 0 | 0
ZONE-R5-Z1W | ROW-R5-Z1W-R2 | 60 |  |  | LL-R5-W | AIRZONE-R5-W | RACK-R5-Z1W-R2-04 | POD-08 | RACKPDU-RACK-R5-Z1W-R2-04-A | RACKPDU-RACK-R5-Z1W-R2-04-B | 60 | 51 | 9 | 72 | 85% | 15% | RPP-R5-A2 | RPP-R5-B2 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R5W | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [6 empty] | 60 | 60 | 60 | 60 | 60 | 60 | 100% | 100% | 100% | 100% | 100% | 100% |  |  | DTC-RACK-R5-Z1W-R2-04 | 56.6667 | 0 | 0 | 0 | 0 | 0 | 0
ZONE-R5-Z1W | ROW-R5-Z1W-R2 | 60 |  |  | LL-R5-W | AIRZONE-R5-W | RACK-R5-Z1W-R2-05 | POD-08 | RACKPDU-RACK-R5-Z1W-R2-05-A | RACKPDU-RACK-R5-Z1W-R2-05-B | 60 | 51 | 9 | 72 | 85% | 15% | RPP-R5-A2 | RPP-R5-B2 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R5W | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [6 empty] | 60 | 60 | 60 | 60 | 60 | 60 | 100% | 100% | 100% | 100% | 100% | 100% |  |  | DTC-RACK-R5-Z1W-R2-05 | 56.6667 | 0 | 0 | 0 | 0 | 0 | 0
ZONE-R5-Z1W | ROW-R5-Z1W-R2 | 60 |  |  | LL-R5-W | AIRZONE-R5-W | RACK-R5-Z1W-R2-06 | POD-08 | RACKPDU-RACK-R5-Z1W-R2-06-A | RACKPDU-RACK-R5-Z1W-R2-06-B | 60 | 51 | 9 | 72 | 85% | 15% | RPP-R5-A2 | RPP-R5-B2 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R5W | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [6 empty] | 60 | 60 | 60 | 60 | 60 | 60 | 100% | 100% | 100% | 100% | 100% | 100% |  |  | DTC-RACK-R5-Z1W-R2-06 | 56.6667 | 0 | 0 | 0 | 0 | 0 | 0
ZONE-R5-Z1W | ROW-R5-Z1W-R2 | 60 |  |  | LL-R5-W | AIRZONE-R5-W | RACK-R5-Z1W-R2-07 | POD-08 | RACKPDU-RACK-R5-Z1W-R2-07-A | RACKPDU-RACK-R5-Z1W-R2-07-B | 60 | 51 | 9 | 72 | 85% | 15% | RPP-R5-A2 | RPP-R5-B2 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R5W | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [6 empty] | 60 | 60 | 60 | 60 | 60 | 60 | 100% | 100% | 100% | 100% | 100% | 100% |  |  | DTC-RACK-R5-Z1W-R2-07 | 56.6667 | 0 | 0 | 0 | 0 | 0 | 0
ZONE-R5-Z1W | ROW-R5-Z1W-R2 | 60 |  |  | LL-R5-W | AIRZONE-R5-W | RACK-R5-Z1W-R2-08 | POD-08 | RACKPDU-RACK-R5-Z1W-R2-08-A | RACKPDU-RACK-R5-Z1W-R2-08-B | 60 | 51 | 9 | 72 | 85% | 15% | RPP-R5-A2 | RPP-R5-B2 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R5W | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [6 empty] | 60 | 60 | 60 | 60 | 60 | 60 | 100% | 100% | 100% | 100% | 100% | 100% |  |  | DTC-RACK-R5-Z1W-R2-08 | 56.6667 | 0 | 0 | 0 | 0 | 0 | 0
ZONE-R5-Z1W | ROW-R5-Z1W-R2 | 60 |  |  | LL-R5-W | AIRZONE-R5-W | RACK-R5-Z1W-R2-09 | POD-08 | RACKPDU-RACK-R5-Z1W-R2-09-A | RACKPDU-RACK-R5-Z1W-R2-09-B | 60 | 51 | 9 | 72 | 85% | 15% | RPP-R5-A2 | RPP-R5-B2 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R5W | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [6 empty] | 60 | 60 | 60 | 60 | 60 | 60 | 100% | 100% | 100% | 100% | 100% | 100% |  |  | DTC-RACK-R5-Z1W-R2-09 | 56.6667 | 0 | 0 | 0 | 0 | 0 | 0
ZONE-R5-Z1W | ROW-R5-Z1W-R2 | 60 |  |  | LL-R5-W | AIRZONE-R5-W | RACK-R5-Z1W-R2-10 | POD-08 | RACKPDU-RACK-R5-Z1W-R2-10-A | RACKPDU-RACK-R5-Z1W-R2-10-B | 60 | 51 | 9 | 72 | 85% | 15% | RPP-R5-A2 | RPP-R5-B2 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R5W | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [6 empty] | 60 | 60 | 60 | 60 | 60 | 60 | 100% | 100% | 100% | 100% | 100% | 100% |  |  | DTC-RACK-R5-Z1W-R2-10 | 56.6667 | 0 | 0 | 0 | 0 | 0 | 0
ZONE-R5-Z1W | ROW-R5-Z1W-R2 | 60 |  |  | LL-R5-W | AIRZONE-R5-W | RACK-R5-Z1W-R2-11 | POD-08 | RACKPDU-RACK-R5-Z1W-R2-11-A | RACKPDU-RACK-R5-Z1W-R2-11-B | 60 | 51 | 9 | 72 | 85% | 15% | RPP-R5-A2 | RPP-R5-B2 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R5W | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [6 empty] | 60 | 60 | 60 | 60 | 60 | 60 | 100% | 100% | 100% | 100% | 100% | 100% |  |  | DTC-RACK-R5-Z1W-R2-11 | 56.6667 | 0 | 0 | 0 | 0 | 0 | 0
ZONE-R5-Z1W | ROW-R5-Z1W-R2 | 60 |  |  | LL-R5-W | AIRZONE-R5-W | RACK-R5-Z1W-R2-12 | POD-08 | RACKPDU-RACK-R5-Z1W-R2-12-A | RACKPDU-RACK-R5-Z1W-R2-12-B | 60 | 51 | 9 | 72 | 85% | 15% | RPP-R5-A2 | RPP-R5-B2 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R5W | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [6 empty] | 60 | 60 | 60 | 60 | 60 | 60 | 100% | 100% | 100% | 100% | 100% | 100% |  |  | DTC-RACK-R5-Z1W-R2-12 | 56.6667 | 0 | 0 | 0 | 0 | 0 | 0
ZONE-R5-Z2E | ROW-R5-Z2E-R1 | 60 |  |  | LL-R5-E | AIRZONE-R5-E | RACK-R5-Z2E-R1-01 | POD-09 | RACKPDU-RACK-R5-Z2E-R1-01-A | RACKPDU-RACK-R5-Z2E-R1-01-B | 60 | 51 | 9 | 72 | 85% | 15% | RPP-R5-A3 | RPP-R5-B3 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R5E | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  |  |  | 60 | 51 | 9 | 60 | 60 | 60 | 60 | 60 | 0 | 100% | 100% | 100% | 100% | 100% | 0% |  |  | DTC-RACK-R5-Z2E-R1-01 | 56.6667 | 0 | 0 | 0 | 0 | 0 | 1
ZONE-R5-Z2E | ROW-R5-Z2E-R1 | 60 |  |  | LL-R5-E | AIRZONE-R5-E | RACK-R5-Z2E-R1-02 | POD-09 | RACKPDU-RACK-R5-Z2E-R1-02-A | RACKPDU-RACK-R5-Z2E-R1-02-B | 60 | 51 | 9 | 72 | 85% | 15% | RPP-R5-A3 | RPP-R5-B3 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R5E | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  |  |  | 60 | 51 | 9 | 60 | 60 | 60 | 60 | 60 | 0 | 100% | 100% | 100% | 100% | 100% | 0% |  |  | DTC-RACK-R5-Z2E-R1-02 | 56.6667 | 0 | 0 | 0 | 0 | 0 | 1
ZONE-R5-Z2E | ROW-R5-Z2E-R1 | 60 |  |  | LL-R5-E | AIRZONE-R5-E | RACK-R5-Z2E-R1-03 | POD-09 | RACKPDU-RACK-R5-Z2E-R1-03-A | RACKPDU-RACK-R5-Z2E-R1-03-B | 60 | 51 | 9 | 72 | 85% | 15% | RPP-R5-A3 | RPP-R5-B3 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R5E | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  |  |  | 60 | 51 | 9 | 60 | 60 | 60 | 60 | 60 | 0 | 100% | 100% | 100% | 100% | 100% | 0% |  |  | DTC-RACK-R5-Z2E-R1-03 | 56.6667 | 0 | 0 | 0 | 0 | 0 | 1
ZONE-R5-Z2E | ROW-R5-Z2E-R1 | 60 |  |  | LL-R5-E | AIRZONE-R5-E | RACK-R5-Z2E-R1-04 | POD-09 | RACKPDU-RACK-R5-Z2E-R1-04-A | RACKPDU-RACK-R5-Z2E-R1-04-B | 60 | 51 | 9 | 72 | 85% | 15% | RPP-R5-A3 | RPP-R5-B3 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R5E | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  |  |  | 60 | 51 | 9 | 60 | 60 | 60 | 60 | 60 | 0 | 100% | 100% | 100% | 100% | 100% | 0% |  |  | DTC-RACK-R5-Z2E-R1-04 | 56.6667 | 0 | 0 | 0 | 0 | 0 | 1
ZONE-R5-Z2E | ROW-R5-Z2E-R1 | 60 |  |  | LL-R5-E | AIRZONE-R5-E | RACK-R5-Z2E-R1-05 | POD-09 | RACKPDU-RACK-R5-Z2E-R1-05-A | RACKPDU-RACK-R5-Z2E-R1-05-B | 60 | 51 | 9 | 72 | 85% | 15% | RPP-R5-A3 | RPP-R5-B3 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R5E | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  |  |  | 60 | 51 | 9 | 60 | 60 | 60 | 60 | 60 | 0 | 100% | 100% | 100% | 100% | 100% | 0% |  |  | DTC-RACK-R5-Z2E-R1-05 | 56.6667 | 0 | 0 | 0 | 0 | 0 | 1
ZONE-R5-Z2E | ROW-R5-Z2E-R1 | 60 |  |  | LL-R5-E | AIRZONE-R5-E | RACK-R5-Z2E-R1-06 | POD-09 | RACKPDU-RACK-R5-Z2E-R1-06-A | RACKPDU-RACK-R5-Z2E-R1-06-B | 60 | 51 | 9 | 72 | 85% | 15% | RPP-R5-A3 | RPP-R5-B3 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R5E | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  |  |  | 60 | 51 | 9 | 60 | 60 | 60 | 60 | 60 | 0 | 100% | 100% | 100% | 100% | 100% | 0% |  |  | DTC-RACK-R5-Z2E-R1-06 | 56.6667 | 0 | 0 | 0 | 0 | 0 | 1
ZONE-R5-Z2E | ROW-R5-Z2E-R1 | 60 |  |  | LL-R5-E | AIRZONE-R5-E | RACK-R5-Z2E-R1-07 | POD-09 | RACKPDU-RACK-R5-Z2E-R1-07-A | RACKPDU-RACK-R5-Z2E-R1-07-B | 60 | 51 | 9 | 72 | 85% | 15% | RPP-R5-A3 | RPP-R5-B3 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R5E | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  |  |  | 60 | 51 | 9 | 60 | 60 | 60 | 60 | 60 | 0 | 100% | 100% | 100% | 100% | 100% | 0% |  |  | DTC-RACK-R5-Z2E-R1-07 | 56.6667 | 0 | 0 | 0 | 0 | 0 | 1
ZONE-R5-Z2E | ROW-R5-Z2E-R1 | 60 |  |  | LL-R5-E | AIRZONE-R5-E | RACK-R5-Z2E-R1-08 | POD-09 | RACKPDU-RACK-R5-Z2E-R1-08-A | RACKPDU-RACK-R5-Z2E-R1-08-B | 60 | 51 | 9 | 72 | 85% | 15% | RPP-R5-A3 | RPP-R5-B3 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R5E | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  |  |  | 60 | 51 | 9 | 60 | 60 | 60 | 60 | 60 | 0 | 100% | 100% | 100% | 100% | 100% | 0% |  |  | DTC-RACK-R5-Z2E-R1-08 | 56.6667 | 0 | 0 | 0 | 0 | 0 | 1
ZONE-R5-Z2E | ROW-R5-Z2E-R1 | 60 |  |  | LL-R5-E | AIRZONE-R5-E | RACK-R5-Z2E-R1-09 | POD-09 | RACKPDU-RACK-R5-Z2E-R1-09-A | RACKPDU-RACK-R5-Z2E-R1-09-B | 60 | 51 | 9 | 72 | 85% | 15% | RPP-R5-A3 | RPP-R5-B3 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R5E | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  |  |  | 60 | 51 | 9 | 60 | 60 | 60 | 60 | 60 | 0 | 100% | 100% | 100% | 100% | 100% | 0% |  |  | DTC-RACK-R5-Z2E-R1-09 | 56.6667 | 0 | 0 | 0 | 0 | 0 | 1
ZONE-R5-Z2E | ROW-R5-Z2E-R1 | 60 |  |  | LL-R5-E | AIRZONE-R5-E | RACK-R5-Z2E-R1-10 | POD-09 | RACKPDU-RACK-R5-Z2E-R1-10-A | RACKPDU-RACK-R5-Z2E-R1-10-B | 60 | 51 | 9 | 72 | 85% | 15% | RPP-R5-A3 | RPP-R5-B3 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R5E | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  |  |  | 60 | 51 | 9 | 60 | 60 | 60 | 60 | 60 | 0 | 100% | 100% | 100% | 100% | 100% | 0% |  |  | DTC-RACK-R5-Z2E-R1-10 | 56.6667 | 0 | 0 | 0 | 0 | 0 | 1
ZONE-R5-Z2E | ROW-R5-Z2E-R1 | 60 |  |  | LL-R5-E | AIRZONE-R5-E | RACK-R5-Z2E-R1-11 | POD-09 | RACKPDU-RACK-R5-Z2E-R1-11-A | RACKPDU-RACK-R5-Z2E-R1-11-B | 60 | 51 | 9 | 72 | 85% | 15% | RPP-R5-A3 | RPP-R5-B3 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R5E | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  |  |  | 60 | 51 | 9 | 60 | 60 | 60 | 60 | 60 | 0 | 100% | 100% | 100% | 100% | 100% | 0% |  |  | DTC-RACK-R5-Z2E-R1-11 | 56.6667 | 0 | 0 | 0 | 0 | 0 | 1
ZONE-R5-Z2E | ROW-R5-Z2E-R1 | 60 |  |  | LL-R5-E | AIRZONE-R5-E | RACK-R5-Z2E-R1-12 | POD-09 | RACKPDU-RACK-R5-Z2E-R1-12-A | RACKPDU-RACK-R5-Z2E-R1-12-B | 60 | 51 | 9 | 72 | 85% | 15% | RPP-R5-A3 | RPP-R5-B3 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R5E | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  |  |  | 60 | 51 | 9 | 60 | 60 | 60 | 60 | 60 | 0 | 100% | 100% | 100% | 100% | 100% | 0% |  |  | DTC-RACK-R5-Z2E-R1-12 | 56.6667 | 0 | 0 | 0 | 0 | 0 | 1
ZONE-R5-Z2E | ROW-R5-Z2E-R2 | 60 |  |  | LL-R5-E | AIRZONE-R5-E | RACK-R5-Z2E-R2-01 | POD-09 | RACKPDU-RACK-R5-Z2E-R2-01-A | RACKPDU-RACK-R5-Z2E-R2-01-B | 60 | 51 | 9 | 72 | 85% | 15% | RPP-R5-A4 | RPP-R5-B4 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R5E | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  |  |  | 60 | 51 | 9 | 60 | 60 | 60 | 60 | 60 | 0 | 100% | 100% | 100% | 100% | 100% | 0% |  |  | DTC-RACK-R5-Z2E-R2-01 | 56.6667 | 0 | 0 | 0 | 0 | 0 | 1
ZONE-R5-Z2E | ROW-R5-Z2E-R2 | 60 |  |  | LL-R5-E | AIRZONE-R5-E | RACK-R5-Z2E-R2-02 | POD-09 | RACKPDU-RACK-R5-Z2E-R2-02-A | RACKPDU-RACK-R5-Z2E-R2-02-B | 60 | 51 | 9 | 72 | 85% | 15% | RPP-R5-A4 | RPP-R5-B4 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R5E | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  |  |  | 60 | 51 | 9 | 60 | 60 | 60 | 60 | 60 | 0 | 100% | 100% | 100% | 100% | 100% | 0% |  |  | DTC-RACK-R5-Z2E-R2-02 | 56.6667 | 0 | 0 | 0 | 0 | 0 | 1
ZONE-R5-Z2E | ROW-R5-Z2E-R2 | 60 |  |  | LL-R5-E | AIRZONE-R5-E | RACK-R5-Z2E-R2-03 | POD-09 | RACKPDU-RACK-R5-Z2E-R2-03-A | RACKPDU-RACK-R5-Z2E-R2-03-B | 60 | 51 | 9 | 72 | 85% | 15% | RPP-R5-A4 | RPP-R5-B4 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R5E | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  |  |  | 60 | 51 | 9 | 60 | 60 | 60 | 60 | 60 | 0 | 100% | 100% | 100% | 100% | 100% | 0% |  |  | DTC-RACK-R5-Z2E-R2-03 | 56.6667 | 0 | 0 | 0 | 0 | 0 | 1
ZONE-R5-Z2E | ROW-R5-Z2E-R2 | 60 |  |  | LL-R5-E | AIRZONE-R5-E | RACK-R5-Z2E-R2-04 | POD-09 | RACKPDU-RACK-R5-Z2E-R2-04-A | RACKPDU-RACK-R5-Z2E-R2-04-B | 60 | 51 | 9 | 72 | 85% | 15% | RPP-R5-A4 | RPP-R5-B4 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R5E | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  |  |  | 60 | 51 | 9 | 60 | 60 | 60 | 60 | 60 | 0 | 100% | 100% | 100% | 100% | 100% | 0% |  |  | DTC-RACK-R5-Z2E-R2-04 | 56.6667 | 0 | 0 | 0 | 0 | 0 | 1
ZONE-R5-Z2E | ROW-R5-Z2E-R2 | 60 |  |  | LL-R5-E | AIRZONE-R5-E | RACK-R5-Z2E-R2-05 | POD-09 | RACKPDU-RACK-R5-Z2E-R2-05-A | RACKPDU-RACK-R5-Z2E-R2-05-B | 60 | 51 | 9 | 72 | 85% | 15% | RPP-R5-A4 | RPP-R5-B4 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R5E | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  |  |  | 60 | 51 | 9 | 60 | 60 | 60 | 60 | 60 | 0 | 100% | 100% | 100% | 100% | 100% | 0% |  |  | DTC-RACK-R5-Z2E-R2-05 | 56.6667 | 0 | 0 | 0 | 0 | 0 | 1
ZONE-R5-Z2E | ROW-R5-Z2E-R2 | 60 |  |  | LL-R5-E | AIRZONE-R5-E | RACK-R5-Z2E-R2-06 | POD-09 | RACKPDU-RACK-R5-Z2E-R2-06-A | RACKPDU-RACK-R5-Z2E-R2-06-B | 60 | 51 | 9 | 72 | 85% | 15% | RPP-R5-A4 | RPP-R5-B4 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R5E | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  |  |  | 60 | 51 | 9 | 60 | 60 | 60 | 60 | 60 | 0 | 100% | 100% | 100% | 100% | 100% | 0% |  |  | DTC-RACK-R5-Z2E-R2-06 | 56.6667 | 0 | 0 | 0 | 0 | 0 | 1
ZONE-R5-Z2E | ROW-R5-Z2E-R2 | 60 |  |  | LL-R5-E | AIRZONE-R5-E | RACK-R5-Z2E-R2-07 | POD-09 | RACKPDU-RACK-R5-Z2E-R2-07-A | RACKPDU-RACK-R5-Z2E-R2-07-B | 60 | 51 | 9 | 72 | 85% | 15% | RPP-R5-A4 | RPP-R5-B4 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R5E | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  |  |  | 60 | 51 | 9 | 60 | 60 | 60 | 60 | 60 | 0 | 100% | 100% | 100% | 100% | 100% | 0% |  |  | DTC-RACK-R5-Z2E-R2-07 | 56.6667 | 0 | 0 | 0 | 0 | 0 | 1
ZONE-R5-Z2E | ROW-R5-Z2E-R2 | 60 |  |  | LL-R5-E | AIRZONE-R5-E | RACK-R5-Z2E-R2-08 | POD-09 | RACKPDU-RACK-R5-Z2E-R2-08-A | RACKPDU-RACK-R5-Z2E-R2-08-B | 60 | 51 | 9 | 72 | 85% | 15% | RPP-R5-A4 | RPP-R5-B4 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R5E | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  |  |  | 60 | 51 | 9 | 60 | 60 | 60 | 60 | 60 | 0 | 100% | 100% | 100% | 100% | 100% | 0% |  |  | DTC-RACK-R5-Z2E-R2-08 | 56.6667 | 0 | 0 | 0 | 0 | 0 | 1
ZONE-R5-Z2E | ROW-R5-Z2E-R2 | 60 |  |  | LL-R5-E | AIRZONE-R5-E | RACK-R5-Z2E-R2-09 | POD-09 | RACKPDU-RACK-R5-Z2E-R2-09-A | RACKPDU-RACK-R5-Z2E-R2-09-B | 60 | 51 | 9 | 72 | 85% | 15% | RPP-R5-A4 | RPP-R5-B4 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R5E | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  |  |  | 60 | 51 | 9 | 60 | 60 | 60 | 60 | 60 | 0 | 100% | 100% | 100% | 100% | 100% | 0% |  |  | DTC-RACK-R5-Z2E-R2-09 | 56.6667 | 0 | 0 | 0 | 0 | 0 | 1
ZONE-R5-Z2E | ROW-R5-Z2E-R2 | 60 |  |  | LL-R5-E | AIRZONE-R5-E | RACK-R5-Z2E-R2-10 | POD-09 | RACKPDU-RACK-R5-Z2E-R2-10-A | RACKPDU-RACK-R5-Z2E-R2-10-B | 60 | 51 | 9 | 72 | 85% | 15% | RPP-R5-A4 | RPP-R5-B4 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R5E | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  |  |  | 60 | 51 | 9 | 60 | 60 | 60 | 60 | 60 | 0 | 100% | 100% | 100% | 100% | 100% | 0% |  |  | DTC-RACK-R5-Z2E-R2-10 | 56.6667 | 0 | 0 | 0 | 0 | 0 | 1
ZONE-R5-Z2E | ROW-R5-Z2E-R2 | 60 |  |  | LL-R5-E | AIRZONE-R5-E | RACK-R5-Z2E-R2-11 | POD-09 | RACKPDU-RACK-R5-Z2E-R2-11-A | RACKPDU-RACK-R5-Z2E-R2-11-B | 60 | 51 | 9 | 72 | 85% | 15% | RPP-R5-A4 | RPP-R5-B4 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R5E | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  |  |  | 60 | 51 | 9 | 60 | 60 | 60 | 60 | 60 | 0 | 100% | 100% | 100% | 100% | 100% | 0% |  |  | DTC-RACK-R5-Z2E-R2-11 | 56.6667 | 0 | 0 | 0 | 0 | 0 | 1
ZONE-R5-Z2E | ROW-R5-Z2E-R2 | 60 |  |  | LL-R5-E | AIRZONE-R5-E | RACK-R5-Z2E-R2-12 | POD-09 | RACKPDU-RACK-R5-Z2E-R2-12-A | RACKPDU-RACK-R5-Z2E-R2-12-B | 60 | 51 | 9 | 72 | 85% | 15% | RPP-R5-A4 | RPP-R5-B4 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R5E | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  |  |  | 15 | 12.75 | 2.25 | 60 | 60 | 60 | 60 | 60 | 45 | 100% | 100% | 100% | 100% | 100% | 75% |  |  | DTC-RACK-R5-Z2E-R2-12 | 56.6667 | 0 | 0 | 0 | 0 | 0 | 1
ZONE-R1-Z1 | ROW-R1-Z1-R1 | 15 |  |  | LL-R1 | AIRZONE-R1 | RACK-R1-Z1-R1-01 | POD-01 | RACKPDU-RACK-R1-Z1-R1-01 |  | 15 | 7.5 | 7.5 | 18 | 50% | 50% | RPP-R1-1 |  | RPDU-R1 |  | UPS-01 |  | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01 | 15 | 7.5 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [18 empty] | RDHX-RACK-R1-Z1-R1-01 | 8.3333 |  |  | 1 | 0 | 0 | 0 | 0 | 0
ZONE-R1-Z1 | ROW-R1-Z1-R1 | 15 |  |  | LL-R1 | AIRZONE-R1 | RACK-R1-Z1-R1-02 | POD-01 | RACKPDU-RACK-R1-Z1-R1-02 |  | 15 | 7.5 | 7.5 | 18 | 50% | 50% | RPP-R1-2 |  | RPDU-R1 |  | UPS-01 |  | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01 | 15 | 7.5 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [18 empty] | RDHX-RACK-R1-Z1-R1-02 | 8.3333 |  |  | 1 | 0 | 0 | 0 | 0 | 0
ZONE-R1-Z1 | ROW-R1-Z1-R1 | 15 |  |  | LL-R1 | AIRZONE-R1 | RACK-R1-Z1-R1-03 | POD-01 | RACKPDU-RACK-R1-Z1-R1-03 |  | 15 | 7.5 | 7.5 | 18 | 50% | 50% | RPP-R2-1 |  | RPDU-R2 |  | UPS-01 |  | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01 | 15 | 7.5 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [18 empty] | RDHX-RACK-R1-Z1-R1-03 | 8.3333 |  |  | 1 | 0 | 0 | 0 | 0 | 0
ZONE-R1-Z1 | ROW-R1-Z1-R1 | 15 |  |  | LL-R1 | AIRZONE-R1 | RACK-R1-Z1-R1-04 | POD-01 | RACKPDU-RACK-R1-Z1-R1-04 |  | 15 | 7.5 | 7.5 | 18 | 50% | 50% | RPP-R2-2 |  | RPDU-R2 |  | UPS-01 |  | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01 | 15 | 7.5 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [18 empty] | RDHX-RACK-R1-Z1-R1-04 | 8.3333 |  |  | 1 | 0 | 0 | 0 | 0 | 0
ZONE-R1-Z1 | ROW-R1-Z1-R1 | 15 |  |  | LL-R1 | AIRZONE-R1 | RACK-R1-Z1-R1-05 | POD-01 | RACKPDU-RACK-R1-Z1-R1-05 |  | 15 | 7.5 | 7.5 | 18 | 50% | 50% | RPP-R1-1 |  | RPDU-R1 |  | UPS-01 |  | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01 | 15 | 7.5 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [18 empty] | RDHX-RACK-R1-Z1-R1-05 | 8.3333 |  |  | 1 | 0 | 0 | 0 | 0 | 0
ZONE-R1-Z1 | ROW-R1-Z1-R1 | 15 |  |  | LL-R1 | AIRZONE-R1 | RACK-R1-Z1-R1-06 | POD-01 | RACKPDU-RACK-R1-Z1-R1-06 |  | 15 | 7.5 | 7.5 | 18 | 50% | 50% | RPP-R1-2 |  | RPDU-R1 |  | UPS-01 |  | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01 | 15 | 7.5 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [18 empty] | RDHX-RACK-R1-Z1-R1-06 | 8.3333 |  |  | 1 | 0 | 0 | 0 | 0 | 0
ZONE-R1-Z1 | ROW-R1-Z1-R2 | 15 |  |  | LL-R1 | AIRZONE-R1 | RACK-R1-Z1-R2-01 | POD-01 | RACKPDU-RACK-R1-Z1-R2-01 |  | 15 | 7.5 | 7.5 | 18 | 50% | 50% | RPP-R2-1 |  | RPDU-R2 |  | UPS-01 |  | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01 | 10 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [18 empty] | RDHX-RACK-R1-Z1-R2-01 | 8.3333 |  |  | 1 | 0 | 0 | 0 | 0 | 0
ZONE-R1-Z1 | ROW-R1-Z1-R2 | 15 |  |  | LL-R1 | AIRZONE-R1 | RACK-R1-Z1-R2-02 | POD-01 | RACKPDU-RACK-R1-Z1-R2-02 |  | 15 | 7.5 | 7.5 | 18 | 50% | 50% | RPP-R2-2 |  | RPDU-R2 |  | UPS-01 |  | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01 | 10 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [18 empty] | RDHX-RACK-R1-Z1-R2-02 | 8.3333 |  |  | 1 | 0 | 0 | 0 | 0 | 0
ZONE-R1-Z1 | ROW-R1-Z1-R2 | 15 |  |  | LL-R1 | AIRZONE-R1 | RACK-R1-Z1-R2-03 | POD-01 | RACKPDU-RACK-R1-Z1-R2-03 |  | 15 | 7.5 | 7.5 | 18 | 50% | 50% | RPP-R1-1 |  | RPDU-R1 |  | UPS-01 |  | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01 | 10 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [18 empty] | RDHX-RACK-R1-Z1-R2-03 | 8.3333 |  |  | 1 | 0 | 0 | 0 | 0 | 0
ZONE-R1-Z1 | ROW-R1-Z1-R2 | 15 |  |  | LL-R1 | AIRZONE-R1 | RACK-R1-Z1-R2-04 | POD-01 | RACKPDU-RACK-R1-Z1-R2-04 |  | 15 | 7.5 | 7.5 | 18 | 50% | 50% | RPP-R1-2 |  | RPDU-R1 |  | UPS-01 |  | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01 | 10 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [18 empty] | RDHX-RACK-R1-Z1-R2-04 | 8.3333 |  |  | 1 | 0 | 0 | 0 | 0 | 0
ZONE-R1-Z1 | ROW-R1-Z1-R2 | 15 |  |  | LL-R1 | AIRZONE-R1 | RACK-R1-Z1-R2-05 | POD-01 | RACKPDU-RACK-R1-Z1-R2-05 |  | 15 | 7.5 | 7.5 | 18 | 50% | 50% | RPP-R2-1 |  | RPDU-R2 |  | UPS-01 |  | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01 | 10 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [18 empty] | RDHX-RACK-R1-Z1-R2-05 | 8.3333 |  |  | 1 | 0 | 0 | 0 | 0 | 0
ZONE-R1-Z1 | ROW-R1-Z1-R2 | 15 |  |  | LL-R1 | AIRZONE-R1 | RACK-R1-Z1-R2-06 | POD-01 | RACKPDU-RACK-R1-Z1-R2-06 |  | 15 | 7.5 | 7.5 | 18 | 50% | 50% | RPP-R2-2 |  | RPDU-R2 |  | UPS-01 |  | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01 | 10 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [18 empty] | RDHX-RACK-R1-Z1-R2-06 | 8.3333 |  |  | 1 | 0 | 0 | 0 | 0 | 0
ZONE-R1-Z2 | ROW-R1-Z2-R1 | 15 |  |  | LL-R1 | AIRZONE-R1 | RACK-R1-Z2-R1-01 | POD-02 | RACKPDU-RACK-R1-Z2-R1-01 |  | 15 | 7.5 | 7.5 | 18 | 50% | 50% | RPP-R1-1 |  | RPDU-R1 |  | UPS-01 |  | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01 | 15 | 7.5 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [18 empty] | RDHX-RACK-R1-Z2-R1-01 | 8.3333 |  |  | 1 | 0 | 0 | 0 | 0 | 0
ZONE-R1-Z2 | ROW-R1-Z2-R1 | 15 |  |  | LL-R1 | AIRZONE-R1 | RACK-R1-Z2-R1-02 | POD-02 | RACKPDU-RACK-R1-Z2-R1-02 |  | 15 | 7.5 | 7.5 | 18 | 50% | 50% | RPP-R1-2 |  | RPDU-R1 |  | UPS-01 |  | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01 | 15 | 7.5 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [18 empty] | RDHX-RACK-R1-Z2-R1-02 | 8.3333 |  |  | 1 | 0 | 0 | 0 | 0 | 0
ZONE-R1-Z2 | ROW-R1-Z2-R1 | 15 |  |  | LL-R1 | AIRZONE-R1 | RACK-R1-Z2-R1-03 | POD-02 | RACKPDU-RACK-R1-Z2-R1-03 |  | 15 | 7.5 | 7.5 | 18 | 50% | 50% | RPP-R2-1 |  | RPDU-R2 |  | UPS-01 |  | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01 | 15 | 7.5 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [18 empty] | RDHX-RACK-R1-Z2-R1-03 | 8.3333 |  |  | 1 | 0 | 0 | 0 | 0 | 0
ZONE-R1-Z2 | ROW-R1-Z2-R1 | 15 |  |  | LL-R1 | AIRZONE-R1 | RACK-R1-Z2-R1-04 | POD-02 | RACKPDU-RACK-R1-Z2-R1-04 |  | 15 | 7.5 | 7.5 | 18 | 50% | 50% | RPP-R2-2 |  | RPDU-R2 |  | UPS-01 |  | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01 | 15 | 7.5 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [18 empty] | RDHX-RACK-R1-Z2-R1-04 | 8.3333 |  |  | 1 | 0 | 0 | 0 | 0 | 0
ZONE-R1-Z2 | ROW-R1-Z2-R1 | 15 |  |  | LL-R1 | AIRZONE-R1 | RACK-R1-Z2-R1-05 | POD-02 | RACKPDU-RACK-R1-Z2-R1-05 |  | 15 | 7.5 | 7.5 | 18 | 50% | 50% | RPP-R1-1 |  | RPDU-R1 |  | UPS-01 |  | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01 | 15 | 7.5 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [18 empty] | RDHX-RACK-R1-Z2-R1-05 | 8.3333 |  |  | 1 | 0 | 0 | 0 | 0 | 0
ZONE-R1-Z2 | ROW-R1-Z2-R1 | 15 |  |  | LL-R1 | AIRZONE-R1 | RACK-R1-Z2-R1-06 | POD-02 | RACKPDU-RACK-R1-Z2-R1-06 |  | 15 | 7.5 | 7.5 | 18 | 50% | 50% | RPP-R1-2 |  | RPDU-R1 |  | UPS-01 |  | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01 | 15 | 7.5 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [18 empty] | RDHX-RACK-R1-Z2-R1-06 | 8.3333 |  |  | 1 | 0 | 0 | 0 | 0 | 0
ZONE-R1-Z2 | ROW-R1-Z2-R2 | 15 |  |  | LL-R1 | AIRZONE-R1 | RACK-R1-Z2-R2-01 | POD-02 | RACKPDU-RACK-R1-Z2-R2-01 |  | 15 | 7.5 | 7.5 | 18 | 50% | 50% | RPP-R2-1 |  | RPDU-R2 |  | UPS-01 |  | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01 | 10 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [18 empty] | RDHX-RACK-R1-Z2-R2-01 | 8.3333 |  |  | 1 | 0 | 0 | 0 | 0 | 0
ZONE-R1-Z2 | ROW-R1-Z2-R2 | 15 |  |  | LL-R1 | AIRZONE-R1 | RACK-R1-Z2-R2-02 | POD-02 | RACKPDU-RACK-R1-Z2-R2-02 |  | 15 | 7.5 | 7.5 | 18 | 50% | 50% | RPP-R2-2 |  | RPDU-R2 |  | UPS-01 |  | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01 | 10 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [18 empty] | RDHX-RACK-R1-Z2-R2-02 | 8.3333 |  |  | 1 | 0 | 0 | 0 | 0 | 0
ZONE-R1-Z2 | ROW-R1-Z2-R2 | 15 |  |  | LL-R1 | AIRZONE-R1 | RACK-R1-Z2-R2-03 | POD-02 | RACKPDU-RACK-R1-Z2-R2-03 |  | 15 | 7.5 | 7.5 | 18 | 50% | 50% | RPP-R1-1 |  | RPDU-R1 |  | UPS-01 |  | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01 | 10 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [18 empty] | RDHX-RACK-R1-Z2-R2-03 | 8.3333 |  |  | 1 | 0 | 0 | 0 | 0 | 0
ZONE-R1-Z2 | ROW-R1-Z2-R2 | 15 |  |  | LL-R1 | AIRZONE-R1 | RACK-R1-Z2-R2-04 | POD-02 | RACKPDU-RACK-R1-Z2-R2-04 |  | 15 | 7.5 | 7.5 | 18 | 50% | 50% | RPP-R1-2 |  | RPDU-R1 |  | UPS-01 |  | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01 | 10 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [18 empty] | RDHX-RACK-R1-Z2-R2-04 | 8.3333 |  |  | 1 | 0 | 0 | 0 | 0 | 0
ZONE-R1-Z2 | ROW-R1-Z2-R2 | 15 |  |  | LL-R1 | AIRZONE-R1 | RACK-R1-Z2-R2-05 | POD-02 | RACKPDU-RACK-R1-Z2-R2-05 |  | 15 | 7.5 | 7.5 | 18 | 50% | 50% | RPP-R2-1 |  | RPDU-R2 |  | UPS-01 |  | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01 | 10 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [18 empty] | RDHX-RACK-R1-Z2-R2-05 | 8.3333 |  |  | 1 | 0 | 0 | 0 | 0 | 0
ZONE-R1-Z2 | ROW-R1-Z2-R2 | 15 |  |  | LL-R1 | AIRZONE-R1 | RACK-R1-Z2-R2-06 | POD-02 | RACKPDU-RACK-R1-Z2-R2-06 |  | 15 | 7.5 | 7.5 | 18 | 50% | 50% | RPP-R2-2 |  | RPDU-R2 |  | UPS-01 |  | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01 | 10 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [18 empty] | RDHX-RACK-R1-Z2-R2-06 | 8.3333 |  |  | 1 | 0 | 0 | 0 | 0 | 0
ZONE-R2-Z1 | ROW-R2-Z1-R1 | 15 |  |  | LL-R2 | AIRZONE-R2 | RACK-R2-Z1-R1-01 | POD-03 | RACKPDU-RACK-R2-Z1-R1-01 |  | 15 | 7.5 | 7.5 | 18 | 50% | 50% | RPP-R1-1 |  | RPDU-R1 |  | UPS-01 |  | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01 | 15 | 7.5 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [20 empty] | DTC-RACK-R2-Z1-R1-01 | 8.3333 | 1 | 0 | 0 | 0 | 0 | 0
ZONE-R2-Z1 | ROW-R2-Z1-R1 | 15 |  |  | LL-R2 | AIRZONE-R2 | RACK-R2-Z1-R1-02 | POD-03 | RACKPDU-RACK-R2-Z1-R1-02 |  | 15 | 7.5 | 7.5 | 18 | 50% | 50% | RPP-R1-2 |  | RPDU-R1 |  | UPS-01 |  | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01 | 15 | 7.5 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [20 empty] | DTC-RACK-R2-Z1-R1-02 | 8.3333 | 1 | 0 | 0 | 0 | 0 | 0
ZONE-R2-Z1 | ROW-R2-Z1-R1 | 15 |  |  | LL-R2 | AIRZONE-R2 | RACK-R2-Z1-R1-03 | POD-03 | RACKPDU-RACK-R2-Z1-R1-03 |  | 15 | 7.5 | 7.5 | 18 | 50% | 50% | RPP-R2-1 |  | RPDU-R2 |  | UPS-01 |  | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01 | 15 | 7.5 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [20 empty] | DTC-RACK-R2-Z1-R1-03 | 8.3333 | 1 | 0 | 0 | 0 | 0 | 0
ZONE-R2-Z1 | ROW-R2-Z1-R1 | 15 |  |  | LL-R2 | AIRZONE-R2 | RACK-R2-Z1-R1-04 | POD-03 | RACKPDU-RACK-R2-Z1-R1-04 |  | 15 | 7.5 | 7.5 | 18 | 50% | 50% | RPP-R2-2 |  | RPDU-R2 |  | UPS-01 |  | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01 | 15 | 7.5 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [20 empty] | DTC-RACK-R2-Z1-R1-04 | 8.3333 | 1 | 0 | 0 | 0 | 0 | 0
ZONE-R2-Z1 | ROW-R2-Z1-R1 | 15 |  |  | LL-R2 | AIRZONE-R2 | RACK-R2-Z1-R1-05 | POD-03 | RACKPDU-RACK-R2-Z1-R1-05 |  | 15 | 7.5 | 7.5 | 18 | 50% | 50% | RPP-R1-1 |  | RPDU-R1 |  | UPS-01 |  | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01 | 15 | 7.5 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [20 empty] | DTC-RACK-R2-Z1-R1-05 | 8.3333 | 1 | 0 | 0 | 0 | 0 | 0
ZONE-R2-Z1 | ROW-R2-Z1-R1 | 15 |  |  | LL-R2 | AIRZONE-R2 | RACK-R2-Z1-R1-06 | POD-03 | RACKPDU-RACK-R2-Z1-R1-06 |  | 15 | 7.5 | 7.5 | 18 | 50% | 50% | RPP-R1-2 |  | RPDU-R1 |  | UPS-01 |  | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01 | 15 | 7.5 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [20 empty] | DTC-RACK-R2-Z1-R1-06 | 8.3333 | 1 | 0 | 0 | 0 | 0 | 0
ZONE-R2-Z1 | ROW-R2-Z1-R2 | 15 |  |  | LL-R2 | AIRZONE-R2 | RACK-R2-Z1-R2-01 | POD-03 | RACKPDU-RACK-R2-Z1-R2-01 |  | 15 | 7.5 | 7.5 | 18 | 50% | 50% | RPP-R2-1 |  | RPDU-R2 |  | UPS-01 |  | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01 | 10 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [20 empty] | DTC-RACK-R2-Z1-R2-01 | 8.3333 | 1 | 0 | 0 | 0 | 0 | 0
ZONE-R2-Z1 | ROW-R2-Z1-R2 | 15 |  |  | LL-R2 | AIRZONE-R2 | RACK-R2-Z1-R2-02 | POD-03 | RACKPDU-RACK-R2-Z1-R2-02 |  | 15 | 7.5 | 7.5 | 18 | 50% | 50% | RPP-R2-2 |  | RPDU-R2 |  | UPS-01 |  | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01 | 10 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [20 empty] | DTC-RACK-R2-Z1-R2-02 | 8.3333 | 1 | 0 | 0 | 0 | 0 | 0
ZONE-R2-Z1 | ROW-R2-Z1-R2 | 15 |  |  | LL-R2 | AIRZONE-R2 | RACK-R2-Z1-R2-03 | POD-03 | RACKPDU-RACK-R2-Z1-R2-03 |  | 15 | 7.5 | 7.5 | 18 | 50% | 50% | RPP-R1-1 |  | RPDU-R1 |  | UPS-01 |  | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01 | 10 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [20 empty] | DTC-RACK-R2-Z1-R2-03 | 8.3333 | 1 | 0 | 0 | 0 | 0 | 0
ZONE-R2-Z1 | ROW-R2-Z1-R2 | 15 |  |  | LL-R2 | AIRZONE-R2 | RACK-R2-Z1-R2-04 | POD-03 | RACKPDU-RACK-R2-Z1-R2-04 |  | 15 | 7.5 | 7.5 | 18 | 50% | 50% | RPP-R1-2 |  | RPDU-R1 |  | UPS-01 |  | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01 | 10 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [20 empty] | DTC-RACK-R2-Z1-R2-04 | 8.3333 | 1 | 0 | 0 | 0 | 0 | 0
ZONE-R2-Z1 | ROW-R2-Z1-R2 | 15 |  |  | LL-R2 | AIRZONE-R2 | RACK-R2-Z1-R2-05 | POD-03 | RACKPDU-RACK-R2-Z1-R2-05 |  | 15 | 7.5 | 7.5 | 18 | 50% | 50% | RPP-R2-1 |  | RPDU-R2 |  | UPS-01 |  | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01 | 10 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [20 empty] | DTC-RACK-R2-Z1-R2-05 | 8.3333 | 1 | 0 | 0 | 0 | 0 | 0
ZONE-R2-Z1 | ROW-R2-Z1-R2 | 15 |  |  | LL-R2 | AIRZONE-R2 | RACK-R2-Z1-R2-06 | POD-03 | RACKPDU-RACK-R2-Z1-R2-06 |  | 15 | 7.5 | 7.5 | 18 | 50% | 50% | RPP-R2-2 |  | RPDU-R2 |  | UPS-01 |  | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01 | 10 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [20 empty] | DTC-RACK-R2-Z1-R2-06 | 8.3333 | 1 | 0 | 0 | 0 | 0 | 0
ZONE-R2-Z2 | ROW-R2-Z2-R1 | 15 |  |  | LL-R2 | AIRZONE-R2 | RACK-R2-Z2-R1-01 | POD-04 | RACKPDU-RACK-R2-Z2-R1-01 |  | 15 | 7.5 | 7.5 | 18 | 50% | 50% | RPP-R1-1 |  | RPDU-R1 |  | UPS-01 |  | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [20 empty] | DTC-RACK-R2-Z2-R1-01 | 8.3333 | 0 | 0 | 0 | 0 | 0 | 0
ZONE-R2-Z2 | ROW-R2-Z2-R1 | 15 |  |  | LL-R2 | AIRZONE-R2 | RACK-R2-Z2-R1-02 | POD-04 | RACKPDU-RACK-R2-Z2-R1-02 |  | 15 | 7.5 | 7.5 | 18 | 50% | 50% | RPP-R1-2 |  | RPDU-R1 |  | UPS-01 |  | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [20 empty] | DTC-RACK-R2-Z2-R1-02 | 8.3333 | 0 | 0 | 0 | 0 | 0 | 0
ZONE-R2-Z2 | ROW-R2-Z2-R1 | 15 |  |  | LL-R2 | AIRZONE-R2 | RACK-R2-Z2-R1-03 | POD-04 | RACKPDU-RACK-R2-Z2-R1-03 |  | 15 | 7.5 | 7.5 | 18 | 50% | 50% | RPP-R2-1 |  | RPDU-R2 |  | UPS-01 |  | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [20 empty] | DTC-RACK-R2-Z2-R1-03 | 8.3333 | 0 | 0 | 0 | 0 | 0 | 0
ZONE-R2-Z2 | ROW-R2-Z2-R1 | 15 |  |  | LL-R2 | AIRZONE-R2 | RACK-R2-Z2-R1-04 | POD-04 | RACKPDU-RACK-R2-Z2-R1-04 |  | 15 | 7.5 | 7.5 | 18 | 50% | 50% | RPP-R2-2 |  | RPDU-R2 |  | UPS-01 |  | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [20 empty] | DTC-RACK-R2-Z2-R1-04 | 8.3333 | 0 | 0 | 0 | 0 | 0 | 0
ZONE-R2-Z2 | ROW-R2-Z2-R1 | 15 |  |  | LL-R2 | AIRZONE-R2 | RACK-R2-Z2-R1-05 | POD-04 | RACKPDU-RACK-R2-Z2-R1-05 |  | 15 | 7.5 | 7.5 | 18 | 50% | 50% | RPP-R1-1 |  | RPDU-R1 |  | UPS-01 |  | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [20 empty] | DTC-RACK-R2-Z2-R1-05 | 8.3333 | 0 | 0 | 0 | 0 | 0 | 0
ZONE-R2-Z2 | ROW-R2-Z2-R1 | 15 |  |  | LL-R2 | AIRZONE-R2 | RACK-R2-Z2-R1-06 | POD-04 | RACKPDU-RACK-R2-Z2-R1-06 |  | 15 | 7.5 | 7.5 | 18 | 50% | 50% | RPP-R1-2 |  | RPDU-R1 |  | UPS-01 |  | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [20 empty] | DTC-RACK-R2-Z2-R1-06 | 8.3333 | 0 | 0 | 0 | 0 | 0 | 0
ZONE-R2-Z2 | ROW-R2-Z2-R2 | 15 |  |  | LL-R2 | AIRZONE-R2 | RACK-R2-Z2-R2-01 | POD-04 | RACKPDU-RACK-R2-Z2-R2-01 |  | 15 | 7.5 | 7.5 | 18 | 50% | 50% | RPP-R2-1 |  | RPDU-R2 |  | UPS-01 |  | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [20 empty] | DTC-RACK-R2-Z2-R2-01 | 8.3333 | 0 | 0 | 0 | 0 | 0 | 0
ZONE-R2-Z2 | ROW-R2-Z2-R2 | 15 |  |  | LL-R2 | AIRZONE-R2 | RACK-R2-Z2-R2-02 | POD-04 | RACKPDU-RACK-R2-Z2-R2-02 |  | 15 | 7.5 | 7.5 | 18 | 50% | 50% | RPP-R2-2 |  | RPDU-R2 |  | UPS-01 |  | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [20 empty] | DTC-RACK-R2-Z2-R2-02 | 8.3333 | 0 | 0 | 0 | 0 | 0 | 0
ZONE-R2-Z2 | ROW-R2-Z2-R2 | 15 |  |  | LL-R2 | AIRZONE-R2 | RACK-R2-Z2-R2-03 | POD-04 | RACKPDU-RACK-R2-Z2-R2-03 |  | 15 | 7.5 | 7.5 | 18 | 50% | 50% | RPP-R1-1 |  | RPDU-R1 |  | UPS-01 |  | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [20 empty] | DTC-RACK-R2-Z2-R2-03 | 8.3333 | 0 | 0 | 0 | 0 | 0 | 0
ZONE-R2-Z2 | ROW-R2-Z2-R2 | 15 |  |  | LL-R2 | AIRZONE-R2 | RACK-R2-Z2-R2-04 | POD-04 | RACKPDU-RACK-R2-Z2-R2-04 |  | 15 | 7.5 | 7.5 | 18 | 50% | 50% | RPP-R1-2 |  | RPDU-R1 |  | UPS-01 |  | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [20 empty] | DTC-RACK-R2-Z2-R2-04 | 8.3333 | 0 | 0 | 0 | 0 | 0 | 0
ZONE-R2-Z2 | ROW-R2-Z2-R2 | 15 |  |  | LL-R2 | AIRZONE-R2 | RACK-R2-Z2-R2-05 | POD-04 | RACKPDU-RACK-R2-Z2-R2-05 |  | 15 | 7.5 | 7.5 | 18 | 50% | 50% | RPP-R2-1 |  | RPDU-R2 |  | UPS-01 |  | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [20 empty] | DTC-RACK-R2-Z2-R2-05 | 8.3333 | 0 | 0 | 0 | 0 | 0 | 0
ZONE-R2-Z2 | ROW-R2-Z2-R2 | 15 |  |  | LL-R2 | AIRZONE-R2 | RACK-R2-Z2-R2-06 | POD-04 | RACKPDU-RACK-R2-Z2-R2-06 |  | 15 | 7.5 | 7.5 | 18 | 50% | 50% | RPP-R2-2 |  | RPDU-R2 |  | UPS-01 |  | BESS-01 | SWGR-01 | SWGR-02 | UTIL-01 | UTIL-02 | GEN-01 | GEN-02 | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [20 empty] | DTC-RACK-R2-Z2-R2-06 | 8.3333 | 0 | 0 | 0 | 0 | 0 | 0

## Load_Margin
Node Type | Node ID | Cluster | Draft ID | Private | Allocated_ITLoad | Allocated_AirCool_Load | Allocated_LiquidCool_Load | TheorMax_ITLoad | TheorMax_AirCool_Load | TheorMax_LiquidCool_Load | Rack_Count | Operational Capacity Name | Operational Capacity | Operating Margin Name | Operating Margin | Operating Margin % Name | Operating Margin % | Device Capacity Name | Device Capacity | Device Capacity Margin Name | Device Capacity Margin | Device Capacity Margin% Name | Device Capacity Margin%
Row | ROW-R1-Z1-R1 |  |  | FALSE | 0 |  |  | 0 |  |  | 0
Row | ROW-R1-Z1-R2 |  |  | FALSE | 0 |  |  | 0 |  |  | 0
Row | ROW-R1-Z2-R1 |  |  | FALSE | 0 |  |  | 0 |  |  | 0
Row | ROW-R1-Z2-R2 |  |  | FALSE | 0 |  |  | 0 |  |  | 0
Row | ROW-R2-Z1-R1 |  |  | FALSE | 0 |  |  | 0 |  |  | 0
Row | ROW-R2-Z1-R2 |  |  | FALSE | 0 |  |  | 0 |  |  | 0
Row | ROW-R2-Z2-R1 |  |  | FALSE | 0 |  |  | 0 |  |  | 0
Row | ROW-R2-Z2-R2 |  |  | FALSE | 0 |  |  | 0 |  |  | 0
Row | ROW-R3-Z1W-R1 |  |  | FALSE | 360 |  |  | 450 |  |  | 12
Row | ROW-R3-Z1W-R2 |  |  | FALSE | 120 |  |  | 150 |  |  | 4
Row | ROW-R3-Z2W-R1 |  |  | FALSE | 360 |  |  | 450 |  |  | 12
Row | ROW-R3-Z2W-R2 |  |  | FALSE | 360 |  |  | 450 |  |  | 12
Row | ROW-R3-Z3W-R1 |  |  | FALSE | 360 |  |  | 450 |  |  | 12
Row | ROW-R3-Z3W-R2 |  |  | FALSE | 0 |  |  | 0 |  |  | 0
Row | ROW-R3-Z4E-R1 |  |  | FALSE | 0 |  |  | 0 |  |  | 0
Row | ROW-R3-Z4E-R2 |  |  | FALSE | 0 |  |  | 0 |  |  | 0
Row | ROW-R3-Z5E-R1 |  |  | FALSE | 0 |  |  | 0 |  |  | 0
Row | ROW-R3-Z5E-R2 |  |  | FALSE | 0 |  |  | 0 |  |  | 0
Row | ROW-R3-Z6E-R1 |  |  | FALSE | 0 |  |  | 0 |  |  | 0
Row | ROW-R3-Z6E-R2 |  |  | FALSE | 0 |  |  | 0 |  |  | 0
Row | ROW-R4-Z1-R1 |  |  | FALSE | 0 |  |  | 0 |  |  | 0
Row | ROW-R4-Z1-R2 |  |  | FALSE | 0 |  |  | 0 |  |  | 0
Row | ROW-R5-Z1W-R1 |  |  | FALSE | 0 |  |  | 0 |  |  | 0
Row | ROW-R5-Z1W-R2 |  |  | FALSE | 0 |  |  | 0 |  |  | 0
Row | ROW-R5-Z2E-R1 |  |  | FALSE | 0 |  |  | 0 |  |  | 0
Row | ROW-R5-Z2E-R2 |  |  | FALSE | 0 |  |  | 0 |  |  | 0
RPP | RPP-R1-1 |  |  | FALSE | 0 |  |  | 0 |  |  | 0 | RPP_Panel_Capacity_(design) | 230 | Device_Capacity_Margin | 230 | Device_Capacity_Margin% | 100%
RPP | RPP-R1-2 |  |  | FALSE | 0 |  |  | 0 |  |  | 0 | RPP_Panel_Capacity_(design) | 230 | Device_Capacity_Margin | 230 | Device_Capacity_Margin% | 100%
RPP | RPP-R2-1 |  |  | FALSE | 0 |  |  | 0 |  |  | 0 | RPP_Panel_Capacity_(design) | 230 | Device_Capacity_Margin | 230 | Device_Capacity_Margin% | 100%
RPP | RPP-R2-2 |  |  | FALSE | 0 |  |  | 0 |  |  | 0 | RPP_Panel_Capacity_(design) | 230 | Device_Capacity_Margin | 230 | Device_Capacity_Margin% | 100%
RPP | RPP-R3-A1 |  |  | FALSE | 960 |  |  | 1200 |  |  | 32 | RPP_Panel_Capacity_(design) | 920 | Device_Capacity_Margin | -40 | Device_Capacity_Margin% | -4.348%
RPP | RPP-R3-A2 |  |  | FALSE | 600 |  |  | 750 |  |  | 20 | RPP_Panel_Capacity_(design) | 920 | Device_Capacity_Margin | 320 | Device_Capacity_Margin% | 34.78%
RPP | RPP-R3-A3 |  |  | FALSE | 0 |  |  | 0 |  |  | 0 | RPP_Panel_Capacity_(design) | 920 | Device_Capacity_Margin | 920 | Device_Capacity_Margin% | 100%
RPP | RPP-R3-A4 |  |  | FALSE | 0 |  |  | 0 |  |  | 0 | RPP_Panel_Capacity_(design) | 920 | Device_Capacity_Margin | 920 | Device_Capacity_Margin% | 100%
RPP | RPP-R4-A5 |  |  | FALSE | 0 |  |  | 0 |  |  | 0 | RPP_Panel_Capacity_(design) | 345 | Device_Capacity_Margin | 345 | Device_Capacity_Margin% | 100%
RPP | RPP-R4-A6 |  |  | FALSE | 0 |  |  | 0 |  |  | 0 | RPP_Panel_Capacity_(design) | 345 | Device_Capacity_Margin | 345 | Device_Capacity_Margin% | 100%
RPP | RPP-R5-A1 |  |  | FALSE | 0 |  |  | 0 |  |  | 0 | RPP_Panel_Capacity_(design) | 920 | Device_Capacity_Margin | 920 | Device_Capacity_Margin% | 100%
RPP | RPP-R5-A2 |  |  | FALSE | 0 |  |  | 0 |  |  | 0 | RPP_Panel_Capacity_(design) | 920 | Device_Capacity_Margin | 920 | Device_Capacity_Margin% | 100%
RPP | RPP-R5-A3 |  |  | FALSE | 0 |  |  | 0 |  |  | 0 | RPP_Panel_Capacity_(design) | 920 | Device_Capacity_Margin | 920 | Device_Capacity_Margin% | 100%
RPP | RPP-R5-A4 |  |  | FALSE | 0 |  |  | 0 |  |  | 0 | RPP_Panel_Capacity_(design) | 920 | Device_Capacity_Margin | 920 | Device_Capacity_Margin% | 100%
RPP | RPP-R3-B1 |  |  | FALSE | 360 |  |  | 450 |  |  | 0 | RPP_Panel_Capacity_(design) | 1380 | Device_Capacity_Margin | 1020 | Device_Capacity_Margin% | 73.91%
RPP | RPP-R3-B2 |  |  | FALSE | 420 |  |  | 525 |  |  | 0 | RPP_Panel_Capacity_(design) | 1380 | Device_Capacity_Margin | 960 | Device_Capacity_Margin% | 69.57%
RPP | RPP-R3-B3 |  |  | FALSE | 780 |  |  | 975 |  |  | 0 | RPP_Panel_Capacity_(design) | 920 | Device_Capacity_Margin | 140 | Device_Capacity_Margin% | 15.22%
RPP | RPP-R3-B4 |  |  | FALSE | 0 |  |  | 0 |  |  | 0 | RPP_Panel_Capacity_(design) | 1380 | Device_Capacity_Margin | 1380 | Device_Capacity_Margin% | 100%
RPP | RPP-R4-B5 |  |  | FALSE | 0 |  |  | 0 |  |  | 0 | RPP_Panel_Capacity_(design) | 345 | Device_Capacity_Margin | 345 | Device_Capacity_Margin% | 100%
RPP | RPP-R4-B6 |  |  | FALSE | 0 |  |  | 0 |  |  | 0 | RPP_Panel_Capacity_(design) | 345 | Device_Capacity_Margin | 345 | Device_Capacity_Margin% | 100%
RPP | RPP-R5-B1 |  |  | FALSE | 0 |  |  | 0 |  |  | 0 | RPP_Panel_Capacity_(design) | 920 | Device_Capacity_Margin | 920 | Device_Capacity_Margin% | 100%
RPP | RPP-R5-B2 |  |  | FALSE | 0 |  |  | 0 |  |  | 0 | RPP_Panel_Capacity_(design) | 920 | Device_Capacity_Margin | 920 | Device_Capacity_Margin% | 100%
RPP | RPP-R5-B3 |  |  | FALSE | 0 |  |  | 0 |  |  | 0 | RPP_Panel_Capacity_(design) | 920 | Device_Capacity_Margin | 920 | Device_Capacity_Margin% | 100%
RPP | RPP-R5-B4 |  |  | FALSE | 0 |  |  | 0 |  |  | 0 | RPP_Panel_Capacity_(design) | 920 | Device_Capacity_Margin | 920 | Device_Capacity_Margin% | 100%
Liquid Loop | LL-R1 |  |  | FALSE |  |  | 0 |  |  | 0 | 0 | LL_Cooling_Capacity | 200 | Local_Capacity_Margin | 200 | Local_Capacity_Margin% | 100%
Liquid Loop | LL-R2 |  |  | FALSE |  |  | 0 |  |  | 0 | 0 | LL_Cooling_Capacity | 200 | Local_Capacity_Margin | 200 | Local_Capacity_Margin% | 100%
Liquid Loop | LL-R3-E |  |  | FALSE |  |  | 0 |  |  | 0 | 0 | LL_Cooling_Capacity | 2000 | Local_Capacity_Margin | 2000 | Local_Capacity_Margin% | 100%
Liquid Loop | LL-R3-W |  |  | FALSE |  |  | 1170 |  |  | 1462.5 | 52 | LL_Cooling_Capacity | 1000 | Local_Capacity_Margin | -170 | Local_Capacity_Margin% | -17%
Liquid Loop | LL-R4 |  |  | FALSE |  |  | 0 |  |  | 0 | 0 | LL_Cooling_Capacity | 500 | Local_Capacity_Margin | 500 | Local_Capacity_Margin% | 100%
Liquid Loop | LL-R5-E |  |  | FALSE |  |  | 0 |  |  | 0 | 0 | LL_Cooling_Capacity | 1500 | Local_Capacity_Margin | 1500 | Local_Capacity_Margin% | 100%
Liquid Loop | LL-R5-W |  |  | FALSE |  |  | 0 |  |  | 0 | 0 | LL_Cooling_Capacity | 1500 | Local_Capacity_Margin | 1500 | Local_Capacity_Margin% | 100%
Air Zone | AIRZONE-R1 |  |  | FALSE |  | 0 |  |  | 0 |  | 0 | AirZone_Cooling_Capacity | 270 | Local_Capacity_Margin | 270 | Local_Capacity_Margin% | 100%
Air Zone | AIRZONE-R2 |  |  | FALSE |  | 0 |  |  | 0 |  | 0 | AirZone_Cooling_Capacity | 270 | Local_Capacity_Margin | 270 | Local_Capacity_Margin% | 100%
Air Zone | AIRZONE-R3-E1 |  |  | FALSE |  | 0 |  |  | 0 |  | 0 | AirZone_Cooling_Capacity | 240 | Local_Capacity_Margin | 240 | Local_Capacity_Margin% | 100%
Air Zone | AIRZONE-R3-E2 |  |  | FALSE |  | 0 |  |  | 0 |  | 0 | AirZone_Cooling_Capacity | 180 | Local_Capacity_Margin | 180 | Local_Capacity_Margin% | 100%
Air Zone | AIRZONE-R3-W1 |  |  | FALSE |  | 300 |  |  | 375 |  | 40 | AirZone_Cooling_Capacity | 240 | Local_Capacity_Margin | -60 | Local_Capacity_Margin% | -25%
Air Zone | AIRZONE-R3-W2 |  |  | FALSE |  | 90 |  |  | 112.5 |  | 12 | AirZone_Cooling_Capacity | 180 | Local_Capacity_Margin | 90 | Local_Capacity_Margin% | 50%
Air Zone | AIRZONE-R4 |  |  | FALSE |  | 0 |  |  | 0 |  | 0 | AirZone_Cooling_Capacity | 180 | Local_Capacity_Margin | 180 | Local_Capacity_Margin% | 100%
Air Zone | AIRZONE-R5-E |  |  | FALSE |  | 0 |  |  | 0 |  | 0 | AirZone_Cooling_Capacity | 270 | Local_Capacity_Margin | 270 | Local_Capacity_Margin% | 100%
Air Zone | AIRZONE-R5-W |  |  | FALSE |  | 0 |  |  | 0 |  | 0 | AirZone_Cooling_Capacity | 270 | Local_Capacity_Margin | 270 | Local_Capacity_Margin% | 100%
Room PDU | RPDU-R1 |  |  | FALSE | 0 |  |  | 0 |  |  | 0 | RPDU_Operational_Cap | 400 | Local_Capacity_Margin | 400 | Local_Capacity_Margin% | 100% | RPDU_Design_Capacity | 480 | Device_Capacity_Margin | 480 | Device_Capacity_Margin% | 100%
Room PDU | RPDU-R2 |  |  | FALSE | 0 |  |  | 0 |  |  | 0 | RPDU_Operational_Cap | 400 | Local_Capacity_Margin | 400 | Local_Capacity_Margin% | 100% | RPDU_Design_Capacity | 480 | Device_Capacity_Margin | 480 | Device_Capacity_Margin% | 100%
Room PDU | RPDU-R3-A |  |  | FALSE | 1560 |  |  | 1950 |  |  | 52 | RPDU_Operational_Cap | 4000 | Local_Capacity_Margin | 2440 | Local_Capacity_Margin% | 61% | RPDU_Design_Capacity | 4000 | Device_Capacity_Margin | 2440 | Device_Capacity_Margin% | 61%
Room PDU | RPDU-R4-A |  |  | FALSE | 0 |  |  | 0 |  |  | 0 | RPDU_Operational_Cap | 2500 | Local_Capacity_Margin | 2500 | Local_Capacity_Margin% | 100% | RPDU_Design_Capacity | 3200 | Device_Capacity_Margin | 3200 | Device_Capacity_Margin% | 100%
Room PDU | RPDU-R5-A |  |  | FALSE | 0 |  |  | 0 |  |  | 0 | RPDU_Operational_Cap | 3000 | Local_Capacity_Margin | 3000 | Local_Capacity_Margin% | 100% | RPDU_Design_Capacity | 3200 | Device_Capacity_Margin | 3200 | Device_Capacity_Margin% | 100%
Room PDU | RPDU-R3-B |  |  | FALSE | 780 |  |  | 975 |  |  | 0 | RPDU_Operational_Cap | 960 | Local_Capacity_Margin | 180 | Local_Capacity_Margin% | 18.75% | RPDU_Design_Capacity | 960 | Device_Capacity_Margin | 180 | Device_Capacity_Margin% | 18.75%
Room PDU | RPDU-R3R4-B |  |  | FALSE | 780 |  |  | 975 |  |  | 0 | RPDU_Operational_Cap | 4000 | Local_Capacity_Margin | 3220 | Local_Capacity_Margin% | 80.5% | RPDU_Design_Capacity | 4000 | Device_Capacity_Margin | 3220 | Device_Capacity_Margin% | 80.5%
Room PDU | RPDU-R5-B |  |  | FALSE | 0 |  |  | 0 |  |  | 0 | RPDU_Operational_Cap | 3000 | Local_Capacity_Margin | 3000 | Local_Capacity_Margin% | 100% | RPDU_Design_Capacity | 3200 | Device_Capacity_Margin | 3200 | Device_Capacity_Margin% | 100%
UPS | UPS-01 |  |  | FALSE | 0 |  |  | 0 |  |  | 0 | UPS_Operational_Cap | 780 | Local_Capacity_Margin | 780 | Local_Capacity_Margin% | 100% | UPS_Design_Capacity | 800 | Device_Capacity_Margin | 800 | Device_Capacity_Margin% | 100%
UPS | UPS-02-A |  |  | FALSE | 1560 |  |  | 1950 |  |  | 52 | UPS_Operational_Cap | 9000 | Local_Capacity_Margin | 7440 | Local_Capacity_Margin% | 82.67% | UPS_Design_Capacity | 9600 | Device_Capacity_Margin | 8040 | Device_Capacity_Margin% | 83.75%
UPS | UPS-02-B |  |  | FALSE | 1560 |  |  | 1950 |  |  | 0 | UPS_Operational_Cap | 9000 | Local_Capacity_Margin | 7440 | Local_Capacity_Margin% | 82.67% | UPS_Design_Capacity | 9600 | Device_Capacity_Margin | 8040 | Device_Capacity_Margin% | 83.75%
Cooling Distribution | CDIST-A-02 |  |  | FALSE |  | 1170 |  |  | 1462.5 |  | 52 |  | 2000 | Local_Capacity_Margin | 2000 | Local_Capacity_Margin% | 100%
Cooling Distribution | CDIST-L-02 |  |  | FALSE |  |  | 390 |  |  | 487.5 | 52 |  | 7000 | Local_Capacity_Margin | 7000 | Local_Capacity_Margin% | 100%
Capacity Cell | CC-R1R2 |  |  | FALSE | 0 |  |  | 0 |  |  | 0 | Capacity_Envelope | 920 | Cell_Margin | 920 | Cell_Margin% | 100%
Capacity Cell | CC-R3 |  |  | FALSE | 1560 |  |  | 1950 |  |  | 52 | Capacity_Envelope | 3680 | Cell_Margin | 2120 | Cell_Margin% | 57.61%
Capacity Cell | CC-R4 |  |  | FALSE | 0 |  |  | 0 |  |  | 0 | Capacity_Envelope | 680 | Cell_Margin | 680 | Cell_Margin% | 100%
Capacity Cell | CC-R5E |  |  | FALSE | 0 |  |  | 0 |  |  | 0 | Capacity_Envelope | 1770 | Cell_Margin | 1770 | Cell_Margin% | 100%
Capacity Cell | CC-R5W |  |  | FALSE | 0 |  |  | 0 |  |  | 0 | Capacity_Envelope | 1770 | Cell_Margin | 1770 | Cell_Margin% | 100%
Row | ROW-R1-Z1-R1 | SJ-Pacific-C01 | SJ-Pacific-C01-PD01 | TRUE | 0 |  |  | 0 |  |  | 0
Row | ROW-R1-Z1-R2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD01 | TRUE | 0 |  |  | 0 |  |  | 0
Row | ROW-R1-Z2-R1 | SJ-Pacific-C01 | SJ-Pacific-C01-PD01 | TRUE | 0 |  |  | 0 |  |  | 0
Row | ROW-R1-Z2-R2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD01 | TRUE | 0 |  |  | 0 |  |  | 0
Row | ROW-R2-Z1-R1 | SJ-Pacific-C01 | SJ-Pacific-C01-PD01 | TRUE | 0 |  |  | 0 |  |  | 0
Row | ROW-R2-Z1-R2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD01 | TRUE | 0 |  |  | 0 |  |  | 0
Row | ROW-R2-Z2-R1 | SJ-Pacific-C01 | SJ-Pacific-C01-PD01 | TRUE | 0 |  |  | 0 |  |  | 0
Row | ROW-R2-Z2-R2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD01 | TRUE | 0 |  |  | 0 |  |  | 0
Row | ROW-R3-Z1W-R1 | SJ-Pacific-C01 | SJ-Pacific-C01-PD01 | TRUE | 240 |  |  | 300 |  |  | 8
Row | ROW-R3-Z1W-R2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD01 | TRUE | 300 |  |  | 375 |  |  | 10
Row | ROW-R3-Z2W-R1 | SJ-Pacific-C01 | SJ-Pacific-C01-PD01 | TRUE | 240 |  |  | 300 |  |  | 8
Row | ROW-R3-Z2W-R2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD01 | TRUE | 120 |  |  | 150 |  |  | 4
Row | ROW-R3-Z3W-R1 | SJ-Pacific-C01 | SJ-Pacific-C01-PD01 | TRUE | 360 |  |  | 450 |  |  | 12
Row | ROW-R3-Z3W-R2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD01 | TRUE | 300 |  |  | 375 |  |  | 10
Row | ROW-R3-Z4E-R1 | SJ-Pacific-C01 | SJ-Pacific-C01-PD01 | TRUE | 0 |  |  | 0 |  |  | 0
Row | ROW-R3-Z4E-R2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD01 | TRUE | 0 |  |  | 0 |  |  | 0
Row | ROW-R3-Z5E-R1 | SJ-Pacific-C01 | SJ-Pacific-C01-PD01 | TRUE | 0 |  |  | 0 |  |  | 0
Row | ROW-R3-Z5E-R2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD01 | TRUE | 0 |  |  | 0 |  |  | 0
Row | ROW-R3-Z6E-R1 | SJ-Pacific-C01 | SJ-Pacific-C01-PD01 | TRUE | 0 |  |  | 0 |  |  | 0
Row | ROW-R3-Z6E-R2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD01 | TRUE | 0 |  |  | 0 |  |  | 0
Row | ROW-R4-Z1-R1 | SJ-Pacific-C01 | SJ-Pacific-C01-PD01 | TRUE | 0 |  |  | 0 |  |  | 0
Row | ROW-R4-Z1-R2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD01 | TRUE | 0 |  |  | 0 |  |  | 0
Row | ROW-R5-Z1W-R1 | SJ-Pacific-C01 | SJ-Pacific-C01-PD01 | TRUE | 0 |  |  | 0 |  |  | 0
Row | ROW-R5-Z1W-R2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD01 | TRUE | 0 |  |  | 0 |  |  | 0
Row | ROW-R5-Z2E-R1 | SJ-Pacific-C01 | SJ-Pacific-C01-PD01 | TRUE | 0 |  |  | 0 |  |  | 0
Row | ROW-R5-Z2E-R2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD01 | TRUE | 0 |  |  | 0 |  |  | 0
RPP | RPP-R1-1 | SJ-Pacific-C01 | SJ-Pacific-C01-PD01 | TRUE | 0 |  |  | 0 |  |  | 0 | RPP_Panel_Capacity_(design) | 230 | Device_Capacity_Margin | 230 | Device_Capacity_Margin% | 100%
RPP | RPP-R1-2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD01 | TRUE | 0 |  |  | 0 |  |  | 0 | RPP_Panel_Capacity_(design) | 230 | Device_Capacity_Margin | 230 | Device_Capacity_Margin% | 100%
RPP | RPP-R2-1 | SJ-Pacific-C01 | SJ-Pacific-C01-PD01 | TRUE | 0 |  |  | 0 |  |  | 0 | RPP_Panel_Capacity_(design) | 230 | Device_Capacity_Margin | 230 | Device_Capacity_Margin% | 100%
RPP | RPP-R2-2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD01 | TRUE | 0 |  |  | 0 |  |  | 0 | RPP_Panel_Capacity_(design) | 230 | Device_Capacity_Margin | 230 | Device_Capacity_Margin% | 100%
RPP | RPP-R3-A1 | SJ-Pacific-C01 | SJ-Pacific-C01-PD01 | TRUE | 660 |  |  | 825 |  |  | 22 | RPP_Panel_Capacity_(design) | 920 | Device_Capacity_Margin | 260 | Device_Capacity_Margin% | 28.26%
RPP | RPP-R3-A2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD01 | TRUE | 900 |  |  | 1125 |  |  | 30 | RPP_Panel_Capacity_(design) | 920 | Device_Capacity_Margin | 20 | Device_Capacity_Margin% | 2.174%
RPP | RPP-R3-A3 | SJ-Pacific-C01 | SJ-Pacific-C01-PD01 | TRUE | 0 |  |  | 0 |  |  | 0 | RPP_Panel_Capacity_(design) | 920 | Device_Capacity_Margin | 920 | Device_Capacity_Margin% | 100%
RPP | RPP-R3-A4 | SJ-Pacific-C01 | SJ-Pacific-C01-PD01 | TRUE | 0 |  |  | 0 |  |  | 0 | RPP_Panel_Capacity_(design) | 920 | Device_Capacity_Margin | 920 | Device_Capacity_Margin% | 100%
RPP | RPP-R4-A5 | SJ-Pacific-C01 | SJ-Pacific-C01-PD01 | TRUE | 0 |  |  | 0 |  |  | 0 | RPP_Panel_Capacity_(design) | 345 | Device_Capacity_Margin | 345 | Device_Capacity_Margin% | 100%
RPP | RPP-R4-A6 | SJ-Pacific-C01 | SJ-Pacific-C01-PD01 | TRUE | 0 |  |  | 0 |  |  | 0 | RPP_Panel_Capacity_(design) | 345 | Device_Capacity_Margin | 345 | Device_Capacity_Margin% | 100%
RPP | RPP-R5-A1 | SJ-Pacific-C01 | SJ-Pacific-C01-PD01 | TRUE | 0 |  |  | 0 |  |  | 0 | RPP_Panel_Capacity_(design) | 920 | Device_Capacity_Margin | 920 | Device_Capacity_Margin% | 100%
RPP | RPP-R5-A2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD01 | TRUE | 0 |  |  | 0 |  |  | 0 | RPP_Panel_Capacity_(design) | 920 | Device_Capacity_Margin | 920 | Device_Capacity_Margin% | 100%
RPP | RPP-R5-A3 | SJ-Pacific-C01 | SJ-Pacific-C01-PD01 | TRUE | 0 |  |  | 0 |  |  | 0 | RPP_Panel_Capacity_(design) | 920 | Device_Capacity_Margin | 920 | Device_Capacity_Margin% | 100%
RPP | RPP-R5-A4 | SJ-Pacific-C01 | SJ-Pacific-C01-PD01 | TRUE | 0 |  |  | 0 |  |  | 0 | RPP_Panel_Capacity_(design) | 920 | Device_Capacity_Margin | 920 | Device_Capacity_Margin% | 100%
RPP | RPP-R3-B1 | SJ-Pacific-C01 | SJ-Pacific-C01-PD01 | TRUE | 360 |  |  | 450 |  |  | 0 | RPP_Panel_Capacity_(design) | 1380 | Device_Capacity_Margin | 1020 | Device_Capacity_Margin% | 73.91%
RPP | RPP-R3-B2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD01 | TRUE | 360 |  |  | 450 |  |  | 0 | RPP_Panel_Capacity_(design) | 1380 | Device_Capacity_Margin | 1020 | Device_Capacity_Margin% | 73.91%
RPP | RPP-R3-B3 | SJ-Pacific-C01 | SJ-Pacific-C01-PD01 | TRUE | 840 |  |  | 1050 |  |  | 0 | RPP_Panel_Capacity_(design) | 920 | Device_Capacity_Margin | 80 | Device_Capacity_Margin% | 8.696%
RPP | RPP-R3-B4 | SJ-Pacific-C01 | SJ-Pacific-C01-PD01 | TRUE | 0 |  |  | 0 |  |  | 0 | RPP_Panel_Capacity_(design) | 1380 | Device_Capacity_Margin | 1380 | Device_Capacity_Margin% | 100%
RPP | RPP-R4-B5 | SJ-Pacific-C01 | SJ-Pacific-C01-PD01 | TRUE | 0 |  |  | 0 |  |  | 0 | RPP_Panel_Capacity_(design) | 345 | Device_Capacity_Margin | 345 | Device_Capacity_Margin% | 100%
RPP | RPP-R4-B6 | SJ-Pacific-C01 | SJ-Pacific-C01-PD01 | TRUE | 0 |  |  | 0 |  |  | 0 | RPP_Panel_Capacity_(design) | 345 | Device_Capacity_Margin | 345 | Device_Capacity_Margin% | 100%
RPP | RPP-R5-B1 | SJ-Pacific-C01 | SJ-Pacific-C01-PD01 | TRUE | 0 |  |  | 0 |  |  | 0 | RPP_Panel_Capacity_(design) | 920 | Device_Capacity_Margin | 920 | Device_Capacity_Margin% | 100%
RPP | RPP-R5-B2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD01 | TRUE | 0 |  |  | 0 |  |  | 0 | RPP_Panel_Capacity_(design) | 920 | Device_Capacity_Margin | 920 | Device_Capacity_Margin% | 100%
RPP | RPP-R5-B3 | SJ-Pacific-C01 | SJ-Pacific-C01-PD01 | TRUE | 0 |  |  | 0 |  |  | 0 | RPP_Panel_Capacity_(design) | 920 | Device_Capacity_Margin | 920 | Device_Capacity_Margin% | 100%
RPP | RPP-R5-B4 | SJ-Pacific-C01 | SJ-Pacific-C01-PD01 | TRUE | 0 |  |  | 0 |  |  | 0 | RPP_Panel_Capacity_(design) | 920 | Device_Capacity_Margin | 920 | Device_Capacity_Margin% | 100%
Liquid Loop | LL-R1 | SJ-Pacific-C01 | SJ-Pacific-C01-PD01 | TRUE |  |  | 0 |  |  | 0 | 0 | LL_Cooling_Capacity | 200 | Local_Capacity_Margin | 200 | Local_Capacity_Margin% | 100%
Liquid Loop | LL-R2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD01 | TRUE |  |  | 0 |  |  | 0 | 0 | LL_Cooling_Capacity | 200 | Local_Capacity_Margin | 200 | Local_Capacity_Margin% | 100%
Liquid Loop | LL-R3-E | SJ-Pacific-C01 | SJ-Pacific-C01-PD01 | TRUE |  |  | 0 |  |  | 0 | 0 | LL_Cooling_Capacity | 2000 | Local_Capacity_Margin | 2000 | Local_Capacity_Margin% | 100%
Liquid Loop | LL-R3-W | SJ-Pacific-C01 | SJ-Pacific-C01-PD01 | TRUE |  |  | 1170 |  |  | 1462.5 | 52 | LL_Cooling_Capacity | 1000 | Local_Capacity_Margin | -170 | Local_Capacity_Margin% | -17%
Liquid Loop | LL-R4 | SJ-Pacific-C01 | SJ-Pacific-C01-PD01 | TRUE |  |  | 0 |  |  | 0 | 0 | LL_Cooling_Capacity | 500 | Local_Capacity_Margin | 500 | Local_Capacity_Margin% | 100%
Liquid Loop | LL-R5-E | SJ-Pacific-C01 | SJ-Pacific-C01-PD01 | TRUE |  |  | 0 |  |  | 0 | 0 | LL_Cooling_Capacity | 1500 | Local_Capacity_Margin | 1500 | Local_Capacity_Margin% | 100%
Liquid Loop | LL-R5-W | SJ-Pacific-C01 | SJ-Pacific-C01-PD01 | TRUE |  |  | 0 |  |  | 0 | 0 | LL_Cooling_Capacity | 1500 | Local_Capacity_Margin | 1500 | Local_Capacity_Margin% | 100%
Air Zone | AIRZONE-R1 | SJ-Pacific-C01 | SJ-Pacific-C01-PD01 | TRUE |  | 0 |  |  | 0 |  | 0 | AirZone_Cooling_Capacity | 270 | Local_Capacity_Margin | 270 | Local_Capacity_Margin% | 100%
Air Zone | AIRZONE-R2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD01 | TRUE |  | 0 |  |  | 0 |  | 0 | AirZone_Cooling_Capacity | 270 | Local_Capacity_Margin | 270 | Local_Capacity_Margin% | 100%
Air Zone | AIRZONE-R3-E1 | SJ-Pacific-C01 | SJ-Pacific-C01-PD01 | TRUE |  | 0 |  |  | 0 |  | 0 | AirZone_Cooling_Capacity | 240 | Local_Capacity_Margin | 240 | Local_Capacity_Margin% | 100%
Air Zone | AIRZONE-R3-E2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD01 | TRUE |  | 0 |  |  | 0 |  | 0 | AirZone_Cooling_Capacity | 180 | Local_Capacity_Margin | 180 | Local_Capacity_Margin% | 100%
Air Zone | AIRZONE-R3-W1 | SJ-Pacific-C01 | SJ-Pacific-C01-PD01 | TRUE |  | 225 |  |  | 281.25 |  | 30 | AirZone_Cooling_Capacity | 240 | Local_Capacity_Margin | 15 | Local_Capacity_Margin% | 6.25%
Air Zone | AIRZONE-R3-W2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD01 | TRUE |  | 165 |  |  | 206.25 |  | 22 | AirZone_Cooling_Capacity | 180 | Local_Capacity_Margin | 15 | Local_Capacity_Margin% | 8.333%
Air Zone | AIRZONE-R4 | SJ-Pacific-C01 | SJ-Pacific-C01-PD01 | TRUE |  | 0 |  |  | 0 |  | 0 | AirZone_Cooling_Capacity | 180 | Local_Capacity_Margin | 180 | Local_Capacity_Margin% | 100%
Air Zone | AIRZONE-R5-E | SJ-Pacific-C01 | SJ-Pacific-C01-PD01 | TRUE |  | 0 |  |  | 0 |  | 0 | AirZone_Cooling_Capacity | 270 | Local_Capacity_Margin | 270 | Local_Capacity_Margin% | 100%
Air Zone | AIRZONE-R5-W | SJ-Pacific-C01 | SJ-Pacific-C01-PD01 | TRUE |  | 0 |  |  | 0 |  | 0 | AirZone_Cooling_Capacity | 270 | Local_Capacity_Margin | 270 | Local_Capacity_Margin% | 100%
Room PDU | RPDU-R1 | SJ-Pacific-C01 | SJ-Pacific-C01-PD01 | TRUE | 0 |  |  | 0 |  |  | 0 | RPDU_Operational_Cap | 400 | Local_Capacity_Margin | 400 | Local_Capacity_Margin% | 100% | RPDU_Design_Capacity | 480 | Device_Capacity_Margin | 480 | Device_Capacity_Margin% | 100%
Room PDU | RPDU-R2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD01 | TRUE | 0 |  |  | 0 |  |  | 0 | RPDU_Operational_Cap | 400 | Local_Capacity_Margin | 400 | Local_Capacity_Margin% | 100% | RPDU_Design_Capacity | 480 | Device_Capacity_Margin | 480 | Device_Capacity_Margin% | 100%
Room PDU | RPDU-R3-A | SJ-Pacific-C01 | SJ-Pacific-C01-PD01 | TRUE | 1560 |  |  | 1950 |  |  | 52 | RPDU_Operational_Cap | 4000 | Local_Capacity_Margin | 2440 | Local_Capacity_Margin% | 61% | RPDU_Design_Capacity | 4000 | Device_Capacity_Margin | 2440 | Device_Capacity_Margin% | 61%
Room PDU | RPDU-R4-A | SJ-Pacific-C01 | SJ-Pacific-C01-PD01 | TRUE | 0 |  |  | 0 |  |  | 0 | RPDU_Operational_Cap | 2500 | Local_Capacity_Margin | 2500 | Local_Capacity_Margin% | 100% | RPDU_Design_Capacity | 3200 | Device_Capacity_Margin | 3200 | Device_Capacity_Margin% | 100%
Room PDU | RPDU-R5-A | SJ-Pacific-C01 | SJ-Pacific-C01-PD01 | TRUE | 0 |  |  | 0 |  |  | 0 | RPDU_Operational_Cap | 3000 | Local_Capacity_Margin | 3000 | Local_Capacity_Margin% | 100% | RPDU_Design_Capacity | 3200 | Device_Capacity_Margin | 3200 | Device_Capacity_Margin% | 100%
Room PDU | RPDU-R3-B | SJ-Pacific-C01 | SJ-Pacific-C01-PD01 | TRUE | 840 |  |  | 1050 |  |  | 0 | RPDU_Operational_Cap | 960 | Local_Capacity_Margin | 120 | Local_Capacity_Margin% | 12.5% | RPDU_Design_Capacity | 960 | Device_Capacity_Margin | 120 | Device_Capacity_Margin% | 12.5%
Room PDU | RPDU-R3R4-B | SJ-Pacific-C01 | SJ-Pacific-C01-PD01 | TRUE | 720 |  |  | 900 |  |  | 0 | RPDU_Operational_Cap | 4000 | Local_Capacity_Margin | 3280 | Local_Capacity_Margin% | 82% | RPDU_Design_Capacity | 4000 | Device_Capacity_Margin | 3280 | Device_Capacity_Margin% | 82%
Room PDU | RPDU-R5-B | SJ-Pacific-C01 | SJ-Pacific-C01-PD01 | TRUE | 0 |  |  | 0 |  |  | 0 | RPDU_Operational_Cap | 3000 | Local_Capacity_Margin | 3000 | Local_Capacity_Margin% | 100% | RPDU_Design_Capacity | 3200 | Device_Capacity_Margin | 3200 | Device_Capacity_Margin% | 100%
UPS | UPS-01 | SJ-Pacific-C01 | SJ-Pacific-C01-PD01 | TRUE | 0 |  |  | 0 |  |  | 0 | UPS_Operational_Cap | 780 | Local_Capacity_Margin | 780 | Local_Capacity_Margin% | 100% | UPS_Design_Capacity | 800 | Device_Capacity_Margin | 800 | Device_Capacity_Margin% | 100%
UPS | UPS-02-A | SJ-Pacific-C01 | SJ-Pacific-C01-PD01 | TRUE | 1560 |  |  | 1950 |  |  | 52 | UPS_Operational_Cap | 9000 | Local_Capacity_Margin | 7440 | Local_Capacity_Margin% | 82.67% | UPS_Design_Capacity | 9600 | Device_Capacity_Margin | 8040 | Device_Capacity_Margin% | 83.75%
UPS | UPS-02-B | SJ-Pacific-C01 | SJ-Pacific-C01-PD01 | TRUE | 1560 |  |  | 1950 |  |  | 0 | UPS_Operational_Cap | 9000 | Local_Capacity_Margin | 7440 | Local_Capacity_Margin% | 82.67% | UPS_Design_Capacity | 9600 | Device_Capacity_Margin | 8040 | Device_Capacity_Margin% | 83.75%
Cooling Distribution | CDIST-A-02 | SJ-Pacific-C01 | SJ-Pacific-C01-PD01 | TRUE |  | 1170 |  |  | 1462.5 |  | 52 |  | 2000 | Local_Capacity_Margin | 2000 | Local_Capacity_Margin% | 100%
Cooling Distribution | CDIST-L-02 | SJ-Pacific-C01 | SJ-Pacific-C01-PD01 | TRUE |  |  | 390 |  |  | 487.5 | 52 |  | 7000 | Local_Capacity_Margin | 7000 | Local_Capacity_Margin% | 100%
Capacity Cell | CC-R1R2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD01 | TRUE | 0 |  |  | 0 |  |  | 0 | Capacity_Envelope | 920 | Cell_Margin | 920 | Cell_Margin% | 100%
Capacity Cell | CC-R3 | SJ-Pacific-C01 | SJ-Pacific-C01-PD01 | TRUE | 1560 |  |  | 1950 |  |  | 52 | Capacity_Envelope | 3680 | Cell_Margin | 2120 | Cell_Margin% | 57.61%
Capacity Cell | CC-R4 | SJ-Pacific-C01 | SJ-Pacific-C01-PD01 | TRUE | 0 |  |  | 0 |  |  | 0 | Capacity_Envelope | 680 | Cell_Margin | 680 | Cell_Margin% | 100%
Capacity Cell | CC-R5E | SJ-Pacific-C01 | SJ-Pacific-C01-PD01 | TRUE | 0 |  |  | 0 |  |  | 0 | Capacity_Envelope | 1770 | Cell_Margin | 1770 | Cell_Margin% | 100%
Capacity Cell | CC-R5W | SJ-Pacific-C01 | SJ-Pacific-C01-PD01 | TRUE | 0 |  |  | 0 |  |  | 0 | Capacity_Envelope | 1770 | Cell_Margin | 1770 | Cell_Margin% | 100%
Row | ROW-R1-Z1-R1 | SJ-Pacific-C01 | SJ-Pacific-C01-PD02 | TRUE | 0 |  |  | 0 |  |  | 0
Row | ROW-R1-Z1-R2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD02 | TRUE | 0 |  |  | 0 |  |  | 0
Row | ROW-R1-Z2-R1 | SJ-Pacific-C01 | SJ-Pacific-C01-PD02 | TRUE | 0 |  |  | 0 |  |  | 0
Row | ROW-R1-Z2-R2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD02 | TRUE | 0 |  |  | 0 |  |  | 0
Row | ROW-R2-Z1-R1 | SJ-Pacific-C01 | SJ-Pacific-C01-PD02 | TRUE | 0 |  |  | 0 |  |  | 0
Row | ROW-R2-Z1-R2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD02 | TRUE | 0 |  |  | 0 |  |  | 0
Row | ROW-R2-Z2-R1 | SJ-Pacific-C01 | SJ-Pacific-C01-PD02 | TRUE | 0 |  |  | 0 |  |  | 0
Row | ROW-R2-Z2-R2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD02 | TRUE | 0 |  |  | 0 |  |  | 0
Row | ROW-R3-Z1W-R1 | SJ-Pacific-C01 | SJ-Pacific-C01-PD02 | TRUE | 0 |  |  | 0 |  |  | 0
Row | ROW-R3-Z1W-R2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD02 | TRUE | 0 |  |  | 0 |  |  | 0
Row | ROW-R3-Z2W-R1 | SJ-Pacific-C01 | SJ-Pacific-C01-PD02 | TRUE | 0 |  |  | 0 |  |  | 0
Row | ROW-R3-Z2W-R2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD02 | TRUE | 0 |  |  | 0 |  |  | 0
Row | ROW-R3-Z3W-R1 | SJ-Pacific-C01 | SJ-Pacific-C01-PD02 | TRUE | 0 |  |  | 0 |  |  | 0
Row | ROW-R3-Z3W-R2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD02 | TRUE | 0 |  |  | 0 |  |  | 0
Row | ROW-R3-Z4E-R1 | SJ-Pacific-C01 | SJ-Pacific-C01-PD02 | TRUE | 240 |  |  | 300 |  |  | 8
Row | ROW-R3-Z4E-R2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD02 | TRUE | 240 |  |  | 300 |  |  | 8
Row | ROW-R3-Z5E-R1 | SJ-Pacific-C01 | SJ-Pacific-C01-PD02 | TRUE | 360 |  |  | 450 |  |  | 12
Row | ROW-R3-Z5E-R2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD02 | TRUE | 360 |  |  | 450 |  |  | 12
Row | ROW-R3-Z6E-R1 | SJ-Pacific-C01 | SJ-Pacific-C01-PD02 | TRUE | 360 |  |  | 450 |  |  | 12
Row | ROW-R3-Z6E-R2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD02 | TRUE | 0 |  |  | 0 |  |  | 0
Row | ROW-R4-Z1-R1 | SJ-Pacific-C01 | SJ-Pacific-C01-PD02 | TRUE | 0 |  |  | 0 |  |  | 0
Row | ROW-R4-Z1-R2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD02 | TRUE | 0 |  |  | 0 |  |  | 0
Row | ROW-R5-Z1W-R1 | SJ-Pacific-C01 | SJ-Pacific-C01-PD02 | TRUE | 0 |  |  | 0 |  |  | 0
Row | ROW-R5-Z1W-R2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD02 | TRUE | 0 |  |  | 0 |  |  | 0
Row | ROW-R5-Z2E-R1 | SJ-Pacific-C01 | SJ-Pacific-C01-PD02 | TRUE | 0 |  |  | 0 |  |  | 0
Row | ROW-R5-Z2E-R2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD02 | TRUE | 0 |  |  | 0 |  |  | 0
RPP | RPP-R1-1 | SJ-Pacific-C01 | SJ-Pacific-C01-PD02 | TRUE | 0 |  |  | 0 |  |  | 0 | RPP_Panel_Capacity_(design) | 230 | Device_Capacity_Margin | 230 | Device_Capacity_Margin% | 100%
RPP | RPP-R1-2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD02 | TRUE | 0 |  |  | 0 |  |  | 0 | RPP_Panel_Capacity_(design) | 230 | Device_Capacity_Margin | 230 | Device_Capacity_Margin% | 100%
RPP | RPP-R2-1 | SJ-Pacific-C01 | SJ-Pacific-C01-PD02 | TRUE | 0 |  |  | 0 |  |  | 0 | RPP_Panel_Capacity_(design) | 230 | Device_Capacity_Margin | 230 | Device_Capacity_Margin% | 100%
RPP | RPP-R2-2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD02 | TRUE | 0 |  |  | 0 |  |  | 0 | RPP_Panel_Capacity_(design) | 230 | Device_Capacity_Margin | 230 | Device_Capacity_Margin% | 100%
RPP | RPP-R3-A1 | SJ-Pacific-C01 | SJ-Pacific-C01-PD02 | TRUE | 0 |  |  | 0 |  |  | 0 | RPP_Panel_Capacity_(design) | 920 | Device_Capacity_Margin | 920 | Device_Capacity_Margin% | 100%
RPP | RPP-R3-A2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD02 | TRUE | 0 |  |  | 0 |  |  | 0 | RPP_Panel_Capacity_(design) | 920 | Device_Capacity_Margin | 920 | Device_Capacity_Margin% | 100%
RPP | RPP-R3-A3 | SJ-Pacific-C01 | SJ-Pacific-C01-PD02 | TRUE | 780 |  |  | 975 |  |  | 26 | RPP_Panel_Capacity_(design) | 920 | Device_Capacity_Margin | 140 | Device_Capacity_Margin% | 15.22%
RPP | RPP-R3-A4 | SJ-Pacific-C01 | SJ-Pacific-C01-PD02 | TRUE | 780 |  |  | 975 |  |  | 26 | RPP_Panel_Capacity_(design) | 920 | Device_Capacity_Margin | 140 | Device_Capacity_Margin% | 15.22%
RPP | RPP-R4-A5 | SJ-Pacific-C01 | SJ-Pacific-C01-PD02 | TRUE | 0 |  |  | 0 |  |  | 0 | RPP_Panel_Capacity_(design) | 345 | Device_Capacity_Margin | 345 | Device_Capacity_Margin% | 100%
RPP | RPP-R4-A6 | SJ-Pacific-C01 | SJ-Pacific-C01-PD02 | TRUE | 0 |  |  | 0 |  |  | 0 | RPP_Panel_Capacity_(design) | 345 | Device_Capacity_Margin | 345 | Device_Capacity_Margin% | 100%
RPP | RPP-R5-A1 | SJ-Pacific-C01 | SJ-Pacific-C01-PD02 | TRUE | 0 |  |  | 0 |  |  | 0 | RPP_Panel_Capacity_(design) | 920 | Device_Capacity_Margin | 920 | Device_Capacity_Margin% | 100%
RPP | RPP-R5-A2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD02 | TRUE | 0 |  |  | 0 |  |  | 0 | RPP_Panel_Capacity_(design) | 920 | Device_Capacity_Margin | 920 | Device_Capacity_Margin% | 100%
RPP | RPP-R5-A3 | SJ-Pacific-C01 | SJ-Pacific-C01-PD02 | TRUE | 0 |  |  | 0 |  |  | 0 | RPP_Panel_Capacity_(design) | 920 | Device_Capacity_Margin | 920 | Device_Capacity_Margin% | 100%
RPP | RPP-R5-A4 | SJ-Pacific-C01 | SJ-Pacific-C01-PD02 | TRUE | 0 |  |  | 0 |  |  | 0 | RPP_Panel_Capacity_(design) | 920 | Device_Capacity_Margin | 920 | Device_Capacity_Margin% | 100%
RPP | RPP-R3-B1 | SJ-Pacific-C01 | SJ-Pacific-C01-PD02 | TRUE | 420 |  |  | 525 |  |  | 0 | RPP_Panel_Capacity_(design) | 1380 | Device_Capacity_Margin | 960 | Device_Capacity_Margin% | 69.57%
RPP | RPP-R3-B2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD02 | TRUE | 240 |  |  | 300 |  |  | 0 | RPP_Panel_Capacity_(design) | 1380 | Device_Capacity_Margin | 1140 | Device_Capacity_Margin% | 82.61%
RPP | RPP-R3-B3 | SJ-Pacific-C01 | SJ-Pacific-C01-PD02 | TRUE | 0 |  |  | 0 |  |  | 0 | RPP_Panel_Capacity_(design) | 920 | Device_Capacity_Margin | 920 | Device_Capacity_Margin% | 100%
RPP | RPP-R3-B4 | SJ-Pacific-C01 | SJ-Pacific-C01-PD02 | TRUE | 900 |  |  | 1125 |  |  | 0 | RPP_Panel_Capacity_(design) | 1380 | Device_Capacity_Margin | 480 | Device_Capacity_Margin% | 34.78%
RPP | RPP-R4-B5 | SJ-Pacific-C01 | SJ-Pacific-C01-PD02 | TRUE | 0 |  |  | 0 |  |  | 0 | RPP_Panel_Capacity_(design) | 345 | Device_Capacity_Margin | 345 | Device_Capacity_Margin% | 100%
RPP | RPP-R4-B6 | SJ-Pacific-C01 | SJ-Pacific-C01-PD02 | TRUE | 0 |  |  | 0 |  |  | 0 | RPP_Panel_Capacity_(design) | 345 | Device_Capacity_Margin | 345 | Device_Capacity_Margin% | 100%
RPP | RPP-R5-B1 | SJ-Pacific-C01 | SJ-Pacific-C01-PD02 | TRUE | 0 |  |  | 0 |  |  | 0 | RPP_Panel_Capacity_(design) | 920 | Device_Capacity_Margin | 920 | Device_Capacity_Margin% | 100%
RPP | RPP-R5-B2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD02 | TRUE | 0 |  |  | 0 |  |  | 0 | RPP_Panel_Capacity_(design) | 920 | Device_Capacity_Margin | 920 | Device_Capacity_Margin% | 100%
RPP | RPP-R5-B3 | SJ-Pacific-C01 | SJ-Pacific-C01-PD02 | TRUE | 0 |  |  | 0 |  |  | 0 | RPP_Panel_Capacity_(design) | 920 | Device_Capacity_Margin | 920 | Device_Capacity_Margin% | 100%
RPP | RPP-R5-B4 | SJ-Pacific-C01 | SJ-Pacific-C01-PD02 | TRUE | 0 |  |  | 0 |  |  | 0 | RPP_Panel_Capacity_(design) | 920 | Device_Capacity_Margin | 920 | Device_Capacity_Margin% | 100%
Liquid Loop | LL-R1 | SJ-Pacific-C01 | SJ-Pacific-C01-PD02 | TRUE |  |  | 0 |  |  | 0 | 0 | LL_Cooling_Capacity | 200 | Local_Capacity_Margin | 200 | Local_Capacity_Margin% | 100%
Liquid Loop | LL-R2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD02 | TRUE |  |  | 0 |  |  | 0 | 0 | LL_Cooling_Capacity | 200 | Local_Capacity_Margin | 200 | Local_Capacity_Margin% | 100%
Liquid Loop | LL-R3-E | SJ-Pacific-C01 | SJ-Pacific-C01-PD02 | TRUE |  |  | 1326 |  |  | 1657.5 | 52 | LL_Cooling_Capacity | 2000 | Local_Capacity_Margin | 674 | Local_Capacity_Margin% | 33.7%
Liquid Loop | LL-R3-W | SJ-Pacific-C01 | SJ-Pacific-C01-PD02 | TRUE |  |  | 0 |  |  | 0 | 0 | LL_Cooling_Capacity | 1000 | Local_Capacity_Margin | 1000 | Local_Capacity_Margin% | 100%
Liquid Loop | LL-R4 | SJ-Pacific-C01 | SJ-Pacific-C01-PD02 | TRUE |  |  | 0 |  |  | 0 | 0 | LL_Cooling_Capacity | 500 | Local_Capacity_Margin | 500 | Local_Capacity_Margin% | 100%
Liquid Loop | LL-R5-E | SJ-Pacific-C01 | SJ-Pacific-C01-PD02 | TRUE |  |  | 0 |  |  | 0 | 0 | LL_Cooling_Capacity | 1500 | Local_Capacity_Margin | 1500 | Local_Capacity_Margin% | 100%
Liquid Loop | LL-R5-W | SJ-Pacific-C01 | SJ-Pacific-C01-PD02 | TRUE |  |  | 0 |  |  | 0 | 0 | LL_Cooling_Capacity | 1500 | Local_Capacity_Margin | 1500 | Local_Capacity_Margin% | 100%
Air Zone | AIRZONE-R1 | SJ-Pacific-C01 | SJ-Pacific-C01-PD02 | TRUE |  | 0 |  |  | 0 |  | 0 | AirZone_Cooling_Capacity | 270 | Local_Capacity_Margin | 270 | Local_Capacity_Margin% | 100%
Air Zone | AIRZONE-R2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD02 | TRUE |  | 0 |  |  | 0 |  | 0 | AirZone_Cooling_Capacity | 270 | Local_Capacity_Margin | 270 | Local_Capacity_Margin% | 100%
Air Zone | AIRZONE-R3-E1 | SJ-Pacific-C01 | SJ-Pacific-C01-PD02 | TRUE |  | 180 |  |  | 225 |  | 40 | AirZone_Cooling_Capacity | 240 | Local_Capacity_Margin | 60 | Local_Capacity_Margin% | 25%
Air Zone | AIRZONE-R3-E2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD02 | TRUE |  | 54 |  |  | 67.5 |  | 12 | AirZone_Cooling_Capacity | 180 | Local_Capacity_Margin | 126 | Local_Capacity_Margin% | 70%
Air Zone | AIRZONE-R3-W1 | SJ-Pacific-C01 | SJ-Pacific-C01-PD02 | TRUE |  | 0 |  |  | 0 |  | 0 | AirZone_Cooling_Capacity | 240 | Local_Capacity_Margin | 240 | Local_Capacity_Margin% | 100%
Air Zone | AIRZONE-R3-W2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD02 | TRUE |  | 0 |  |  | 0 |  | 0 | AirZone_Cooling_Capacity | 180 | Local_Capacity_Margin | 180 | Local_Capacity_Margin% | 100%
Air Zone | AIRZONE-R4 | SJ-Pacific-C01 | SJ-Pacific-C01-PD02 | TRUE |  | 0 |  |  | 0 |  | 0 | AirZone_Cooling_Capacity | 180 | Local_Capacity_Margin | 180 | Local_Capacity_Margin% | 100%
Air Zone | AIRZONE-R5-E | SJ-Pacific-C01 | SJ-Pacific-C01-PD02 | TRUE |  | 0 |  |  | 0 |  | 0 | AirZone_Cooling_Capacity | 270 | Local_Capacity_Margin | 270 | Local_Capacity_Margin% | 100%
Air Zone | AIRZONE-R5-W | SJ-Pacific-C01 | SJ-Pacific-C01-PD02 | TRUE |  | 0 |  |  | 0 |  | 0 | AirZone_Cooling_Capacity | 270 | Local_Capacity_Margin | 270 | Local_Capacity_Margin% | 100%
Room PDU | RPDU-R1 | SJ-Pacific-C01 | SJ-Pacific-C01-PD02 | TRUE | 0 |  |  | 0 |  |  | 0 | RPDU_Operational_Cap | 400 | Local_Capacity_Margin | 400 | Local_Capacity_Margin% | 100% | RPDU_Design_Capacity | 480 | Device_Capacity_Margin | 480 | Device_Capacity_Margin% | 100%
Room PDU | RPDU-R2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD02 | TRUE | 0 |  |  | 0 |  |  | 0 | RPDU_Operational_Cap | 400 | Local_Capacity_Margin | 400 | Local_Capacity_Margin% | 100% | RPDU_Design_Capacity | 480 | Device_Capacity_Margin | 480 | Device_Capacity_Margin% | 100%
Room PDU | RPDU-R3-A | SJ-Pacific-C01 | SJ-Pacific-C01-PD02 | TRUE | 1560 |  |  | 1950 |  |  | 52 | RPDU_Operational_Cap | 4000 | Local_Capacity_Margin | 2440 | Local_Capacity_Margin% | 61% | RPDU_Design_Capacity | 4000 | Device_Capacity_Margin | 2440 | Device_Capacity_Margin% | 61%
Room PDU | RPDU-R4-A | SJ-Pacific-C01 | SJ-Pacific-C01-PD02 | TRUE | 0 |  |  | 0 |  |  | 0 | RPDU_Operational_Cap | 2500 | Local_Capacity_Margin | 2500 | Local_Capacity_Margin% | 100% | RPDU_Design_Capacity | 3200 | Device_Capacity_Margin | 3200 | Device_Capacity_Margin% | 100%
Room PDU | RPDU-R5-A | SJ-Pacific-C01 | SJ-Pacific-C01-PD02 | TRUE | 0 |  |  | 0 |  |  | 0 | RPDU_Operational_Cap | 3000 | Local_Capacity_Margin | 3000 | Local_Capacity_Margin% | 100% | RPDU_Design_Capacity | 3200 | Device_Capacity_Margin | 3200 | Device_Capacity_Margin% | 100%
Room PDU | RPDU-R3-B | SJ-Pacific-C01 | SJ-Pacific-C01-PD02 | TRUE | 0 |  |  | 0 |  |  | 0 | RPDU_Operational_Cap | 960 | Local_Capacity_Margin | 960 | Local_Capacity_Margin% | 100% | RPDU_Design_Capacity | 960 | Device_Capacity_Margin | 960 | Device_Capacity_Margin% | 100%
Room PDU | RPDU-R3R4-B | SJ-Pacific-C01 | SJ-Pacific-C01-PD02 | TRUE | 1560 |  |  | 1950 |  |  | 0 | RPDU_Operational_Cap | 4000 | Local_Capacity_Margin | 2440 | Local_Capacity_Margin% | 61% | RPDU_Design_Capacity | 4000 | Device_Capacity_Margin | 2440 | Device_Capacity_Margin% | 61%
Room PDU | RPDU-R5-B | SJ-Pacific-C01 | SJ-Pacific-C01-PD02 | TRUE | 0 |  |  | 0 |  |  | 0 | RPDU_Operational_Cap | 3000 | Local_Capacity_Margin | 3000 | Local_Capacity_Margin% | 100% | RPDU_Design_Capacity | 3200 | Device_Capacity_Margin | 3200 | Device_Capacity_Margin% | 100%
UPS | UPS-01 | SJ-Pacific-C01 | SJ-Pacific-C01-PD02 | TRUE | 0 |  |  | 0 |  |  | 0 | UPS_Operational_Cap | 780 | Local_Capacity_Margin | 780 | Local_Capacity_Margin% | 100% | UPS_Design_Capacity | 800 | Device_Capacity_Margin | 800 | Device_Capacity_Margin% | 100%
UPS | UPS-02-A | SJ-Pacific-C01 | SJ-Pacific-C01-PD02 | TRUE | 1560 |  |  | 1950 |  |  | 52 | UPS_Operational_Cap | 9000 | Local_Capacity_Margin | 7440 | Local_Capacity_Margin% | 82.67% | UPS_Design_Capacity | 9600 | Device_Capacity_Margin | 8040 | Device_Capacity_Margin% | 83.75%
UPS | UPS-02-B | SJ-Pacific-C01 | SJ-Pacific-C01-PD02 | TRUE | 1560 |  |  | 1950 |  |  | 0 | UPS_Operational_Cap | 9000 | Local_Capacity_Margin | 7440 | Local_Capacity_Margin% | 82.67% | UPS_Design_Capacity | 9600 | Device_Capacity_Margin | 8040 | Device_Capacity_Margin% | 83.75%
Cooling Distribution | CDIST-A-02 | SJ-Pacific-C01 | SJ-Pacific-C01-PD02 | TRUE |  | 1326 |  |  | 1657.5 |  | 52 |  | 2000 | Local_Capacity_Margin | 2000 | Local_Capacity_Margin% | 100%
Cooling Distribution | CDIST-L-02 | SJ-Pacific-C01 | SJ-Pacific-C01-PD02 | TRUE |  |  | 234 |  |  | 292.5 | 52 |  | 7000 | Local_Capacity_Margin | 7000 | Local_Capacity_Margin% | 100%
Capacity Cell | CC-R1R2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD02 | TRUE | 0 |  |  | 0 |  |  | 0 | Capacity_Envelope | 920 | Cell_Margin | 920 | Cell_Margin% | 100%
Capacity Cell | CC-R3 | SJ-Pacific-C01 | SJ-Pacific-C01-PD02 | TRUE | 1560 |  |  | 1950 |  |  | 52 | Capacity_Envelope | 3680 | Cell_Margin | 2120 | Cell_Margin% | 57.61%
Capacity Cell | CC-R4 | SJ-Pacific-C01 | SJ-Pacific-C01-PD02 | TRUE | 0 |  |  | 0 |  |  | 0 | Capacity_Envelope | 680 | Cell_Margin | 680 | Cell_Margin% | 100%
Capacity Cell | CC-R5E | SJ-Pacific-C01 | SJ-Pacific-C01-PD02 | TRUE | 0 |  |  | 0 |  |  | 0 | Capacity_Envelope | 1770 | Cell_Margin | 1770 | Cell_Margin% | 100%
Capacity Cell | CC-R5W | SJ-Pacific-C01 | SJ-Pacific-C01-PD02 | TRUE | 0 |  |  | 0 |  |  | 0 | Capacity_Envelope | 1770 | Cell_Margin | 1770 | Cell_Margin% | 100%
Row | ROW-R1-Z1-R1 | SJ-Pacific-C01 | SJ-Pacific-C01-PD03 | TRUE | 0 |  |  | 0 |  |  | 0
Row | ROW-R1-Z1-R2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD03 | TRUE | 0 |  |  | 0 |  |  | 0
Row | ROW-R1-Z2-R1 | SJ-Pacific-C01 | SJ-Pacific-C01-PD03 | TRUE | 0 |  |  | 0 |  |  | 0
Row | ROW-R1-Z2-R2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD03 | TRUE | 0 |  |  | 0 |  |  | 0
Row | ROW-R2-Z1-R1 | SJ-Pacific-C01 | SJ-Pacific-C01-PD03 | TRUE | 0 |  |  | 0 |  |  | 0
Row | ROW-R2-Z1-R2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD03 | TRUE | 0 |  |  | 0 |  |  | 0
Row | ROW-R2-Z2-R1 | SJ-Pacific-C01 | SJ-Pacific-C01-PD03 | TRUE | 0 |  |  | 0 |  |  | 0
Row | ROW-R2-Z2-R2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD03 | TRUE | 0 |  |  | 0 |  |  | 0
Row | ROW-R3-Z1W-R1 | SJ-Pacific-C01 | SJ-Pacific-C01-PD03 | TRUE | 0 |  |  | 0 |  |  | 0
Row | ROW-R3-Z1W-R2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD03 | TRUE | 0 |  |  | 0 |  |  | 0
Row | ROW-R3-Z2W-R1 | SJ-Pacific-C01 | SJ-Pacific-C01-PD03 | TRUE | 0 |  |  | 0 |  |  | 0
Row | ROW-R3-Z2W-R2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD03 | TRUE | 0 |  |  | 0 |  |  | 0
Row | ROW-R3-Z3W-R1 | SJ-Pacific-C01 | SJ-Pacific-C01-PD03 | TRUE | 0 |  |  | 0 |  |  | 0
Row | ROW-R3-Z3W-R2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD03 | TRUE | 0 |  |  | 0 |  |  | 0
Row | ROW-R3-Z4E-R1 | SJ-Pacific-C01 | SJ-Pacific-C01-PD03 | TRUE | 360 |  |  | 450 |  |  | 12
Row | ROW-R3-Z4E-R2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD03 | TRUE | 360 |  |  | 450 |  |  | 12
Row | ROW-R3-Z5E-R1 | SJ-Pacific-C01 | SJ-Pacific-C01-PD03 | TRUE | 360 |  |  | 450 |  |  | 12
Row | ROW-R3-Z5E-R2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD03 | TRUE | 0 |  |  | 0 |  |  | 0
Row | ROW-R3-Z6E-R1 | SJ-Pacific-C01 | SJ-Pacific-C01-PD03 | TRUE | 360 |  |  | 450 |  |  | 12
Row | ROW-R3-Z6E-R2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD03 | TRUE | 120 |  |  | 150 |  |  | 4
Row | ROW-R4-Z1-R1 | SJ-Pacific-C01 | SJ-Pacific-C01-PD03 | TRUE | 0 |  |  | 0 |  |  | 0
Row | ROW-R4-Z1-R2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD03 | TRUE | 0 |  |  | 0 |  |  | 0
Row | ROW-R5-Z1W-R1 | SJ-Pacific-C01 | SJ-Pacific-C01-PD03 | TRUE | 0 |  |  | 0 |  |  | 0
Row | ROW-R5-Z1W-R2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD03 | TRUE | 0 |  |  | 0 |  |  | 0
Row | ROW-R5-Z2E-R1 | SJ-Pacific-C01 | SJ-Pacific-C01-PD03 | TRUE | 0 |  |  | 0 |  |  | 0
Row | ROW-R5-Z2E-R2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD03 | TRUE | 0 |  |  | 0 |  |  | 0
RPP | RPP-R1-1 | SJ-Pacific-C01 | SJ-Pacific-C01-PD03 | TRUE | 0 |  |  | 0 |  |  | 0 | RPP_Panel_Capacity_(design) | 230 | Device_Capacity_Margin | 230 | Device_Capacity_Margin% | 100%
RPP | RPP-R1-2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD03 | TRUE | 0 |  |  | 0 |  |  | 0 | RPP_Panel_Capacity_(design) | 230 | Device_Capacity_Margin | 230 | Device_Capacity_Margin% | 100%
RPP | RPP-R2-1 | SJ-Pacific-C01 | SJ-Pacific-C01-PD03 | TRUE | 0 |  |  | 0 |  |  | 0 | RPP_Panel_Capacity_(design) | 230 | Device_Capacity_Margin | 230 | Device_Capacity_Margin% | 100%
RPP | RPP-R2-2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD03 | TRUE | 0 |  |  | 0 |  |  | 0 | RPP_Panel_Capacity_(design) | 230 | Device_Capacity_Margin | 230 | Device_Capacity_Margin% | 100%
RPP | RPP-R3-A1 | SJ-Pacific-C01 | SJ-Pacific-C01-PD03 | TRUE | 120 |  |  | 150 |  |  | 4 | RPP_Panel_Capacity_(design) | 920 | Device_Capacity_Margin | 800 | Device_Capacity_Margin% | 86.96%
RPP | RPP-R3-A2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD03 | TRUE | 120 |  |  | 150 |  |  | 4 | RPP_Panel_Capacity_(design) | 920 | Device_Capacity_Margin | 800 | Device_Capacity_Margin% | 86.96%
RPP | RPP-R3-A3 | SJ-Pacific-C01 | SJ-Pacific-C01-PD03 | TRUE | 660 |  |  | 825 |  |  | 22 | RPP_Panel_Capacity_(design) | 920 | Device_Capacity_Margin | 260 | Device_Capacity_Margin% | 28.26%
RPP | RPP-R3-A4 | SJ-Pacific-C01 | SJ-Pacific-C01-PD03 | TRUE | 660 |  |  | 825 |  |  | 22 | RPP_Panel_Capacity_(design) | 920 | Device_Capacity_Margin | 260 | Device_Capacity_Margin% | 28.26%
RPP | RPP-R4-A5 | SJ-Pacific-C01 | SJ-Pacific-C01-PD03 | TRUE | 0 |  |  | 0 |  |  | 0 | RPP_Panel_Capacity_(design) | 345 | Device_Capacity_Margin | 345 | Device_Capacity_Margin% | 100%
RPP | RPP-R4-A6 | SJ-Pacific-C01 | SJ-Pacific-C01-PD03 | TRUE | 0 |  |  | 0 |  |  | 0 | RPP_Panel_Capacity_(design) | 345 | Device_Capacity_Margin | 345 | Device_Capacity_Margin% | 100%
RPP | RPP-R5-A1 | SJ-Pacific-C01 | SJ-Pacific-C01-PD03 | TRUE | 0 |  |  | 0 |  |  | 0 | RPP_Panel_Capacity_(design) | 920 | Device_Capacity_Margin | 920 | Device_Capacity_Margin% | 100%
RPP | RPP-R5-A2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD03 | TRUE | 0 |  |  | 0 |  |  | 0 | RPP_Panel_Capacity_(design) | 920 | Device_Capacity_Margin | 920 | Device_Capacity_Margin% | 100%
RPP | RPP-R5-A3 | SJ-Pacific-C01 | SJ-Pacific-C01-PD03 | TRUE | 0 |  |  | 0 |  |  | 0 | RPP_Panel_Capacity_(design) | 920 | Device_Capacity_Margin | 920 | Device_Capacity_Margin% | 100%
RPP | RPP-R5-A4 | SJ-Pacific-C01 | SJ-Pacific-C01-PD03 | TRUE | 0 |  |  | 0 |  |  | 0 | RPP_Panel_Capacity_(design) | 920 | Device_Capacity_Margin | 920 | Device_Capacity_Margin% | 100%
RPP | RPP-R3-B1 | SJ-Pacific-C01 | SJ-Pacific-C01-PD03 | TRUE | 540 |  |  | 675 |  |  | 0 | RPP_Panel_Capacity_(design) | 1380 | Device_Capacity_Margin | 840 | Device_Capacity_Margin% | 60.87%
RPP | RPP-R3-B2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD03 | TRUE | 300 |  |  | 375 |  |  | 0 | RPP_Panel_Capacity_(design) | 1380 | Device_Capacity_Margin | 1080 | Device_Capacity_Margin% | 78.26%
RPP | RPP-R3-B3 | SJ-Pacific-C01 | SJ-Pacific-C01-PD03 | TRUE | 0 |  |  | 0 |  |  | 0 | RPP_Panel_Capacity_(design) | 920 | Device_Capacity_Margin | 920 | Device_Capacity_Margin% | 100%
RPP | RPP-R3-B4 | SJ-Pacific-C01 | SJ-Pacific-C01-PD03 | TRUE | 720 |  |  | 900 |  |  | 0 | RPP_Panel_Capacity_(design) | 1380 | Device_Capacity_Margin | 660 | Device_Capacity_Margin% | 47.83%
RPP | RPP-R4-B5 | SJ-Pacific-C01 | SJ-Pacific-C01-PD03 | TRUE | 0 |  |  | 0 |  |  | 0 | RPP_Panel_Capacity_(design) | 345 | Device_Capacity_Margin | 345 | Device_Capacity_Margin% | 100%
RPP | RPP-R4-B6 | SJ-Pacific-C01 | SJ-Pacific-C01-PD03 | TRUE | 0 |  |  | 0 |  |  | 0 | RPP_Panel_Capacity_(design) | 345 | Device_Capacity_Margin | 345 | Device_Capacity_Margin% | 100%
RPP | RPP-R5-B1 | SJ-Pacific-C01 | SJ-Pacific-C01-PD03 | TRUE | 0 |  |  | 0 |  |  | 0 | RPP_Panel_Capacity_(design) | 920 | Device_Capacity_Margin | 920 | Device_Capacity_Margin% | 100%
RPP | RPP-R5-B2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD03 | TRUE | 0 |  |  | 0 |  |  | 0 | RPP_Panel_Capacity_(design) | 920 | Device_Capacity_Margin | 920 | Device_Capacity_Margin% | 100%
RPP | RPP-R5-B3 | SJ-Pacific-C01 | SJ-Pacific-C01-PD03 | TRUE | 0 |  |  | 0 |  |  | 0 | RPP_Panel_Capacity_(design) | 920 | Device_Capacity_Margin | 920 | Device_Capacity_Margin% | 100%
RPP | RPP-R5-B4 | SJ-Pacific-C01 | SJ-Pacific-C01-PD03 | TRUE | 0 |  |  | 0 |  |  | 0 | RPP_Panel_Capacity_(design) | 920 | Device_Capacity_Margin | 920 | Device_Capacity_Margin% | 100%
Liquid Loop | LL-R1 | SJ-Pacific-C01 | SJ-Pacific-C01-PD03 | TRUE |  |  | 0 |  |  | 0 | 0 | LL_Cooling_Capacity | 200 | Local_Capacity_Margin | 200 | Local_Capacity_Margin% | 100%
Liquid Loop | LL-R2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD03 | TRUE |  |  | 0 |  |  | 0 | 0 | LL_Cooling_Capacity | 200 | Local_Capacity_Margin | 200 | Local_Capacity_Margin% | 100%
Liquid Loop | LL-R3-E | SJ-Pacific-C01 | SJ-Pacific-C01-PD03 | TRUE |  |  | 1326 |  |  | 1657.5 | 52 | LL_Cooling_Capacity | 2000 | Local_Capacity_Margin | 674 | Local_Capacity_Margin% | 33.7%
Liquid Loop | LL-R3-W | SJ-Pacific-C01 | SJ-Pacific-C01-PD03 | TRUE |  |  | 0 |  |  | 0 | 0 | LL_Cooling_Capacity | 1000 | Local_Capacity_Margin | 1000 | Local_Capacity_Margin% | 100%
Liquid Loop | LL-R4 | SJ-Pacific-C01 | SJ-Pacific-C01-PD03 | TRUE |  |  | 0 |  |  | 0 | 0 | LL_Cooling_Capacity | 500 | Local_Capacity_Margin | 500 | Local_Capacity_Margin% | 100%
Liquid Loop | LL-R5-E | SJ-Pacific-C01 | SJ-Pacific-C01-PD03 | TRUE |  |  | 0 |  |  | 0 | 0 | LL_Cooling_Capacity | 1500 | Local_Capacity_Margin | 1500 | Local_Capacity_Margin% | 100%
Liquid Loop | LL-R5-W | SJ-Pacific-C01 | SJ-Pacific-C01-PD03 | TRUE |  |  | 0 |  |  | 0 | 0 | LL_Cooling_Capacity | 1500 | Local_Capacity_Margin | 1500 | Local_Capacity_Margin% | 100%
Air Zone | AIRZONE-R1 | SJ-Pacific-C01 | SJ-Pacific-C01-PD03 | TRUE |  | 0 |  |  | 0 |  | 0 | AirZone_Cooling_Capacity | 270 | Local_Capacity_Margin | 270 | Local_Capacity_Margin% | 100%
Air Zone | AIRZONE-R2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD03 | TRUE |  | 0 |  |  | 0 |  | 0 | AirZone_Cooling_Capacity | 270 | Local_Capacity_Margin | 270 | Local_Capacity_Margin% | 100%
Air Zone | AIRZONE-R3-E1 | SJ-Pacific-C01 | SJ-Pacific-C01-PD03 | TRUE |  | 162 |  |  | 202.5 |  | 36 | AirZone_Cooling_Capacity | 240 | Local_Capacity_Margin | 78 | Local_Capacity_Margin% | 32.5%
Air Zone | AIRZONE-R3-E2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD03 | TRUE |  | 72 |  |  | 90 |  | 16 | AirZone_Cooling_Capacity | 180 | Local_Capacity_Margin | 108 | Local_Capacity_Margin% | 60%
Air Zone | AIRZONE-R3-W1 | SJ-Pacific-C01 | SJ-Pacific-C01-PD03 | TRUE |  | 0 |  |  | 0 |  | 0 | AirZone_Cooling_Capacity | 240 | Local_Capacity_Margin | 240 | Local_Capacity_Margin% | 100%
Air Zone | AIRZONE-R3-W2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD03 | TRUE |  | 0 |  |  | 0 |  | 0 | AirZone_Cooling_Capacity | 180 | Local_Capacity_Margin | 180 | Local_Capacity_Margin% | 100%
Air Zone | AIRZONE-R4 | SJ-Pacific-C01 | SJ-Pacific-C01-PD03 | TRUE |  | 0 |  |  | 0 |  | 0 | AirZone_Cooling_Capacity | 180 | Local_Capacity_Margin | 180 | Local_Capacity_Margin% | 100%
Air Zone | AIRZONE-R5-E | SJ-Pacific-C01 | SJ-Pacific-C01-PD03 | TRUE |  | 0 |  |  | 0 |  | 0 | AirZone_Cooling_Capacity | 270 | Local_Capacity_Margin | 270 | Local_Capacity_Margin% | 100%
Air Zone | AIRZONE-R5-W | SJ-Pacific-C01 | SJ-Pacific-C01-PD03 | TRUE |  | 0 |  |  | 0 |  | 0 | AirZone_Cooling_Capacity | 270 | Local_Capacity_Margin | 270 | Local_Capacity_Margin% | 100%
Room PDU | RPDU-R1 | SJ-Pacific-C01 | SJ-Pacific-C01-PD03 | TRUE | 0 |  |  | 0 |  |  | 0 | RPDU_Operational_Cap | 400 | Local_Capacity_Margin | 400 | Local_Capacity_Margin% | 100% | RPDU_Design_Capacity | 480 | Device_Capacity_Margin | 480 | Device_Capacity_Margin% | 100%
Room PDU | RPDU-R2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD03 | TRUE | 0 |  |  | 0 |  |  | 0 | RPDU_Operational_Cap | 400 | Local_Capacity_Margin | 400 | Local_Capacity_Margin% | 100% | RPDU_Design_Capacity | 480 | Device_Capacity_Margin | 480 | Device_Capacity_Margin% | 100%
Room PDU | RPDU-R3-A | SJ-Pacific-C01 | SJ-Pacific-C01-PD03 | TRUE | 1560 |  |  | 1950 |  |  | 52 | RPDU_Operational_Cap | 4000 | Local_Capacity_Margin | 2440 | Local_Capacity_Margin% | 61% | RPDU_Design_Capacity | 4000 | Device_Capacity_Margin | 2440 | Device_Capacity_Margin% | 61%
Room PDU | RPDU-R4-A | SJ-Pacific-C01 | SJ-Pacific-C01-PD03 | TRUE | 0 |  |  | 0 |  |  | 0 | RPDU_Operational_Cap | 2500 | Local_Capacity_Margin | 2500 | Local_Capacity_Margin% | 100% | RPDU_Design_Capacity | 3200 | Device_Capacity_Margin | 3200 | Device_Capacity_Margin% | 100%
Room PDU | RPDU-R5-A | SJ-Pacific-C01 | SJ-Pacific-C01-PD03 | TRUE | 0 |  |  | 0 |  |  | 0 | RPDU_Operational_Cap | 3000 | Local_Capacity_Margin | 3000 | Local_Capacity_Margin% | 100% | RPDU_Design_Capacity | 3200 | Device_Capacity_Margin | 3200 | Device_Capacity_Margin% | 100%
Room PDU | RPDU-R3-B | SJ-Pacific-C01 | SJ-Pacific-C01-PD03 | TRUE | 0 |  |  | 0 |  |  | 0 | RPDU_Operational_Cap | 960 | Local_Capacity_Margin | 960 | Local_Capacity_Margin% | 100% | RPDU_Design_Capacity | 960 | Device_Capacity_Margin | 960 | Device_Capacity_Margin% | 100%
Room PDU | RPDU-R3R4-B | SJ-Pacific-C01 | SJ-Pacific-C01-PD03 | TRUE | 1560 |  |  | 1950 |  |  | 0 | RPDU_Operational_Cap | 4000 | Local_Capacity_Margin | 2440 | Local_Capacity_Margin% | 61% | RPDU_Design_Capacity | 4000 | Device_Capacity_Margin | 2440 | Device_Capacity_Margin% | 61%
Room PDU | RPDU-R5-B | SJ-Pacific-C01 | SJ-Pacific-C01-PD03 | TRUE | 0 |  |  | 0 |  |  | 0 | RPDU_Operational_Cap | 3000 | Local_Capacity_Margin | 3000 | Local_Capacity_Margin% | 100% | RPDU_Design_Capacity | 3200 | Device_Capacity_Margin | 3200 | Device_Capacity_Margin% | 100%
UPS | UPS-01 | SJ-Pacific-C01 | SJ-Pacific-C01-PD03 | TRUE | 0 |  |  | 0 |  |  | 0 | UPS_Operational_Cap | 780 | Local_Capacity_Margin | 780 | Local_Capacity_Margin% | 100% | UPS_Design_Capacity | 800 | Device_Capacity_Margin | 800 | Device_Capacity_Margin% | 100%
UPS | UPS-02-A | SJ-Pacific-C01 | SJ-Pacific-C01-PD03 | TRUE | 1560 |  |  | 1950 |  |  | 52 | UPS_Operational_Cap | 9000 | Local_Capacity_Margin | 7440 | Local_Capacity_Margin% | 82.67% | UPS_Design_Capacity | 9600 | Device_Capacity_Margin | 8040 | Device_Capacity_Margin% | 83.75%
UPS | UPS-02-B | SJ-Pacific-C01 | SJ-Pacific-C01-PD03 | TRUE | 1560 |  |  | 1950 |  |  | 0 | UPS_Operational_Cap | 9000 | Local_Capacity_Margin | 7440 | Local_Capacity_Margin% | 82.67% | UPS_Design_Capacity | 9600 | Device_Capacity_Margin | 8040 | Device_Capacity_Margin% | 83.75%
Cooling Distribution | CDIST-A-02 | SJ-Pacific-C01 | SJ-Pacific-C01-PD03 | TRUE |  | 1326 |  |  | 1657.5 |  | 52 |  | 2000 | Local_Capacity_Margin | 2000 | Local_Capacity_Margin% | 100%
Cooling Distribution | CDIST-L-02 | SJ-Pacific-C01 | SJ-Pacific-C01-PD03 | TRUE |  |  | 234 |  |  | 292.5 | 52 |  | 7000 | Local_Capacity_Margin | 7000 | Local_Capacity_Margin% | 100%
Capacity Cell | CC-R1R2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD03 | TRUE | 0 |  |  | 0 |  |  | 0 | Capacity_Envelope | 920 | Cell_Margin | 920 | Cell_Margin% | 100%
Capacity Cell | CC-R3 | SJ-Pacific-C01 | SJ-Pacific-C01-PD03 | TRUE | 1560 |  |  | 1950 |  |  | 52 | Capacity_Envelope | 3680 | Cell_Margin | 2120 | Cell_Margin% | 57.61%
Capacity Cell | CC-R4 | SJ-Pacific-C01 | SJ-Pacific-C01-PD03 | TRUE | 0 |  |  | 0 |  |  | 0 | Capacity_Envelope | 680 | Cell_Margin | 680 | Cell_Margin% | 100%
Capacity Cell | CC-R5E | SJ-Pacific-C01 | SJ-Pacific-C01-PD03 | TRUE | 0 |  |  | 0 |  |  | 0 | Capacity_Envelope | 1770 | Cell_Margin | 1770 | Cell_Margin% | 100%
Capacity Cell | CC-R5W | SJ-Pacific-C01 | SJ-Pacific-C01-PD03 | TRUE | 0 |  |  | 0 |  |  | 0 | Capacity_Envelope | 1770 | Cell_Margin | 1770 | Cell_Margin% | 100%
Row | ROW-R1-Z1-R1 | SJ-Pacific-C01 | SJ-Pacific-C01-PD04 | TRUE | 0 |  |  | 0 |  |  | 0
Row | ROW-R1-Z1-R2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD04 | TRUE | 0 |  |  | 0 |  |  | 0
Row | ROW-R1-Z2-R1 | SJ-Pacific-C01 | SJ-Pacific-C01-PD04 | TRUE | 0 |  |  | 0 |  |  | 0
Row | ROW-R1-Z2-R2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD04 | TRUE | 0 |  |  | 0 |  |  | 0
Row | ROW-R2-Z1-R1 | SJ-Pacific-C01 | SJ-Pacific-C01-PD04 | TRUE | 0 |  |  | 0 |  |  | 0
Row | ROW-R2-Z1-R2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD04 | TRUE | 0 |  |  | 0 |  |  | 0
Row | ROW-R2-Z2-R1 | SJ-Pacific-C01 | SJ-Pacific-C01-PD04 | TRUE | 0 |  |  | 0 |  |  | 0
Row | ROW-R2-Z2-R2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD04 | TRUE | 0 |  |  | 0 |  |  | 0
Row | ROW-R3-Z1W-R1 | SJ-Pacific-C01 | SJ-Pacific-C01-PD04 | TRUE | 0 |  |  | 0 |  |  | 0
Row | ROW-R3-Z1W-R2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD04 | TRUE | 0 |  |  | 0 |  |  | 0
Row | ROW-R3-Z2W-R1 | SJ-Pacific-C01 | SJ-Pacific-C01-PD04 | TRUE | 0 |  |  | 0 |  |  | 0
Row | ROW-R3-Z2W-R2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD04 | TRUE | 0 |  |  | 0 |  |  | 0
Row | ROW-R3-Z3W-R1 | SJ-Pacific-C01 | SJ-Pacific-C01-PD04 | TRUE | 0 |  |  | 0 |  |  | 0
Row | ROW-R3-Z3W-R2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD04 | TRUE | 0 |  |  | 0 |  |  | 0
Row | ROW-R3-Z4E-R1 | SJ-Pacific-C01 | SJ-Pacific-C01-PD04 | TRUE | 0 |  |  | 0 |  |  | 0
Row | ROW-R3-Z4E-R2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD04 | TRUE | 0 |  |  | 0 |  |  | 0
Row | ROW-R3-Z5E-R1 | SJ-Pacific-C01 | SJ-Pacific-C01-PD04 | TRUE | 0 |  |  | 0 |  |  | 0
Row | ROW-R3-Z5E-R2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD04 | TRUE | 0 |  |  | 0 |  |  | 0
Row | ROW-R3-Z6E-R1 | SJ-Pacific-C01 | SJ-Pacific-C01-PD04 | TRUE | 0 |  |  | 0 |  |  | 0
Row | ROW-R3-Z6E-R2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD04 | TRUE | 0 |  |  | 0 |  |  | 0
Row | ROW-R4-Z1-R1 | SJ-Pacific-C01 | SJ-Pacific-C01-PD04 | TRUE | 0 |  |  | 0 |  |  | 0
Row | ROW-R4-Z1-R2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD04 | TRUE | 0 |  |  | 0 |  |  | 0
Row | ROW-R5-Z1W-R1 | SJ-Pacific-C01 | SJ-Pacific-C01-PD04 | TRUE | 0 |  |  | 0 |  |  | 0
Row | ROW-R5-Z1W-R2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD04 | TRUE | 0 |  |  | 0 |  |  | 0
Row | ROW-R5-Z2E-R1 | SJ-Pacific-C01 | SJ-Pacific-C01-PD04 | TRUE | 720 |  |  | 900 |  |  | 12
Row | ROW-R5-Z2E-R2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD04 | TRUE | 675 |  |  | 843.75 |  |  | 12
RPP | RPP-R1-1 | SJ-Pacific-C01 | SJ-Pacific-C01-PD04 | TRUE | 0 |  |  | 0 |  |  | 0 | RPP_Panel_Capacity_(design) | 180 | Device_Capacity_Margin | 180 | Device_Capacity_Margin% | 100%
RPP | RPP-R1-2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD04 | TRUE | 0 |  |  | 0 |  |  | 0 | RPP_Panel_Capacity_(design) | 180 | Device_Capacity_Margin | 180 | Device_Capacity_Margin% | 100%
RPP | RPP-R2-1 | SJ-Pacific-C01 | SJ-Pacific-C01-PD04 | TRUE | 0 |  |  | 0 |  |  | 0 | RPP_Panel_Capacity_(design) | 180 | Device_Capacity_Margin | 180 | Device_Capacity_Margin% | 100%
RPP | RPP-R2-2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD04 | TRUE | 0 |  |  | 0 |  |  | 0 | RPP_Panel_Capacity_(design) | 180 | Device_Capacity_Margin | 180 | Device_Capacity_Margin% | 100%
RPP | RPP-R3-A1 | SJ-Pacific-C01 | SJ-Pacific-C01-PD04 | TRUE | 0 |  |  | 0 |  |  | 0 | RPP_Panel_Capacity_(design) | 1260 | Device_Capacity_Margin | 1260 | Device_Capacity_Margin% | 100%
RPP | RPP-R3-A2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD04 | TRUE | 0 |  |  | 0 |  |  | 0 | RPP_Panel_Capacity_(design) | 1260 | Device_Capacity_Margin | 1260 | Device_Capacity_Margin% | 100%
RPP | RPP-R3-A3 | SJ-Pacific-C01 | SJ-Pacific-C01-PD04 | TRUE | 0 |  |  | 0 |  |  | 0 | RPP_Panel_Capacity_(design) | 1440 | Device_Capacity_Margin | 1440 | Device_Capacity_Margin% | 100%
RPP | RPP-R3-A4 | SJ-Pacific-C01 | SJ-Pacific-C01-PD04 | TRUE | 0 |  |  | 0 |  |  | 0 | RPP_Panel_Capacity_(design) | 1440 | Device_Capacity_Margin | 1440 | Device_Capacity_Margin% | 100%
RPP | RPP-R4-A5 | SJ-Pacific-C01 | SJ-Pacific-C01-PD04 | TRUE | 0 |  |  | 0 |  |  | 0 | RPP_Panel_Capacity_(design) | 240 | Device_Capacity_Margin | 240 | Device_Capacity_Margin% | 100%
RPP | RPP-R4-A6 | SJ-Pacific-C01 | SJ-Pacific-C01-PD04 | TRUE | 0 |  |  | 0 |  |  | 0 | RPP_Panel_Capacity_(design) | 240 | Device_Capacity_Margin | 240 | Device_Capacity_Margin% | 100%
RPP | RPP-R5-A1 | SJ-Pacific-C01 | SJ-Pacific-C01-PD04 | TRUE | 0 |  |  | 0 |  |  | 0 | RPP_Panel_Capacity_(design) | 720 | Device_Capacity_Margin | 720 | Device_Capacity_Margin% | 100%
RPP | RPP-R5-A2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD04 | TRUE | 0 |  |  | 0 |  |  | 0 | RPP_Panel_Capacity_(design) | 720 | Device_Capacity_Margin | 720 | Device_Capacity_Margin% | 100%
RPP | RPP-R5-A3 | SJ-Pacific-C01 | SJ-Pacific-C01-PD04 | TRUE | 720 |  |  | 900 |  |  | 12 | RPP_Panel_Capacity_(design) | 720 | Device_Capacity_Margin | 0 | Device_Capacity_Margin% | 0%
RPP | RPP-R5-A4 | SJ-Pacific-C01 | SJ-Pacific-C01-PD04 | TRUE | 675 |  |  | 843.75 |  |  | 12 | RPP_Panel_Capacity_(design) | 720 | Device_Capacity_Margin | 45 | Device_Capacity_Margin% | 6.25%
RPP | RPP-R3-B1 | SJ-Pacific-C01 | SJ-Pacific-C01-PD04 | TRUE | 0 |  |  | 0 |  |  | 0 | RPP_Panel_Capacity_(design) | 1350 | Device_Capacity_Margin | 1350 | Device_Capacity_Margin% | 100%
RPP | RPP-R3-B2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD04 | TRUE | 0 |  |  | 0 |  |  | 0 | RPP_Panel_Capacity_(design) | 1350 | Device_Capacity_Margin | 1350 | Device_Capacity_Margin% | 100%
RPP | RPP-R3-B3 | SJ-Pacific-C01 | SJ-Pacific-C01-PD04 | TRUE | 0 |  |  | 0 |  |  | 0 | RPP_Panel_Capacity_(design) | 1080 | Device_Capacity_Margin | 1080 | Device_Capacity_Margin% | 100%
RPP | RPP-R3-B4 | SJ-Pacific-C01 | SJ-Pacific-C01-PD04 | TRUE | 0 |  |  | 0 |  |  | 0 | RPP_Panel_Capacity_(design) | 1620 | Device_Capacity_Margin | 1620 | Device_Capacity_Margin% | 100%
RPP | RPP-R4-B5 | SJ-Pacific-C01 | SJ-Pacific-C01-PD04 | TRUE | 0 |  |  | 0 |  |  | 0 | RPP_Panel_Capacity_(design) | 240 | Device_Capacity_Margin | 240 | Device_Capacity_Margin% | 100%
RPP | RPP-R4-B6 | SJ-Pacific-C01 | SJ-Pacific-C01-PD04 | TRUE | 0 |  |  | 0 |  |  | 0 | RPP_Panel_Capacity_(design) | 240 | Device_Capacity_Margin | 240 | Device_Capacity_Margin% | 100%
RPP | RPP-R5-B1 | SJ-Pacific-C01 | SJ-Pacific-C01-PD04 | TRUE | 0 |  |  | 0 |  |  | 0 | RPP_Panel_Capacity_(design) | 720 | Device_Capacity_Margin | 720 | Device_Capacity_Margin% | 100%
RPP | RPP-R5-B2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD04 | TRUE | 0 |  |  | 0 |  |  | 0 | RPP_Panel_Capacity_(design) | 720 | Device_Capacity_Margin | 720 | Device_Capacity_Margin% | 100%
RPP | RPP-R5-B3 | SJ-Pacific-C01 | SJ-Pacific-C01-PD04 | TRUE | 720 |  |  | 900 |  |  | 0 | RPP_Panel_Capacity_(design) | 720 | Device_Capacity_Margin | 0 | Device_Capacity_Margin% | 0%
RPP | RPP-R5-B4 | SJ-Pacific-C01 | SJ-Pacific-C01-PD04 | TRUE | 675 |  |  | 843.75 |  |  | 0 | RPP_Panel_Capacity_(design) | 720 | Device_Capacity_Margin | 45 | Device_Capacity_Margin% | 6.25%
Liquid Loop | LL-R1 | SJ-Pacific-C01 | SJ-Pacific-C01-PD04 | TRUE |  |  | 0 |  |  | 0 | 0 | LL_Cooling_Capacity | 180 | Local_Capacity_Margin | 180 | Local_Capacity_Margin% | 100%
Liquid Loop | LL-R2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD04 | TRUE |  |  | 0 |  |  | 0 | 0 | LL_Cooling_Capacity | 180 | Local_Capacity_Margin | 180 | Local_Capacity_Margin% | 100%
Liquid Loop | LL-R3-E | SJ-Pacific-C01 | SJ-Pacific-C01-PD04 | TRUE |  |  | 0 |  |  | 0 | 0 | LL_Cooling_Capacity | 2754 | Local_Capacity_Margin | 2754 | Local_Capacity_Margin% | 100%
Liquid Loop | LL-R3-W | SJ-Pacific-C01 | SJ-Pacific-C01-PD04 | TRUE |  |  | 0 |  |  | 0 | 0 | LL_Cooling_Capacity | 1620 | Local_Capacity_Margin | 1620 | Local_Capacity_Margin% | 100%
Liquid Loop | LL-R4 | SJ-Pacific-C01 | SJ-Pacific-C01-PD04 | TRUE |  |  | 0 |  |  | 0 | 0 | LL_Cooling_Capacity | 336 | Local_Capacity_Margin | 336 | Local_Capacity_Margin% | 100%
Liquid Loop | LL-R5-E | SJ-Pacific-C01 | SJ-Pacific-C01-PD04 | TRUE |  |  | 1185.75 |  |  | 1482.1875 | 24 | LL_Cooling_Capacity | 1224 | Local_Capacity_Margin | 38.25 | Local_Capacity_Margin% | 3.125%
Liquid Loop | LL-R5-W | SJ-Pacific-C01 | SJ-Pacific-C01-PD04 | TRUE |  |  | 0 |  |  | 0 | 0 | LL_Cooling_Capacity | 1224 | Local_Capacity_Margin | 1224 | Local_Capacity_Margin% | 100%
Air Zone | AIRZONE-R1 | SJ-Pacific-C01 | SJ-Pacific-C01-PD04 | TRUE |  | 0 |  |  | 0 |  | 0 | AirZone_Cooling_Capacity | 180 | Local_Capacity_Margin | 180 | Local_Capacity_Margin% | 100%
Air Zone | AIRZONE-R2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD04 | TRUE |  | 0 |  |  | 0 |  | 0 | AirZone_Cooling_Capacity | 180 | Local_Capacity_Margin | 180 | Local_Capacity_Margin% | 100%
Air Zone | AIRZONE-R3-E1 | SJ-Pacific-C01 | SJ-Pacific-C01-PD04 | TRUE |  | 0 |  |  | 0 |  | 0 | AirZone_Cooling_Capacity | 324 | Local_Capacity_Margin | 324 | Local_Capacity_Margin% | 100%
Air Zone | AIRZONE-R3-E2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD04 | TRUE |  | 0 |  |  | 0 |  | 0 | AirZone_Cooling_Capacity | 162 | Local_Capacity_Margin | 162 | Local_Capacity_Margin% | 100%
Air Zone | AIRZONE-R3-W1 | SJ-Pacific-C01 | SJ-Pacific-C01-PD04 | TRUE |  | 0 |  |  | 0 |  | 0 | AirZone_Cooling_Capacity | 360 | Local_Capacity_Margin | 360 | Local_Capacity_Margin% | 100%
Air Zone | AIRZONE-R3-W2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD04 | TRUE |  | 0 |  |  | 0 |  | 0 | AirZone_Cooling_Capacity | 180 | Local_Capacity_Margin | 180 | Local_Capacity_Margin% | 100%
Air Zone | AIRZONE-R4 | SJ-Pacific-C01 | SJ-Pacific-C01-PD04 | TRUE |  | 0 |  |  | 0 |  | 0 | AirZone_Cooling_Capacity | 144 | Local_Capacity_Margin | 144 | Local_Capacity_Margin% | 100%
Air Zone | AIRZONE-R5-E | SJ-Pacific-C01 | SJ-Pacific-C01-PD04 | TRUE |  | 209.25 |  |  | 261.5625 |  | 24 | AirZone_Cooling_Capacity | 216 | Local_Capacity_Margin | 6.75 | Local_Capacity_Margin% | 3.125%
Air Zone | AIRZONE-R5-W | SJ-Pacific-C01 | SJ-Pacific-C01-PD04 | TRUE |  | 0 |  |  | 0 |  | 0 | AirZone_Cooling_Capacity | 216 | Local_Capacity_Margin | 216 | Local_Capacity_Margin% | 100%
Room PDU | RPDU-R1 | SJ-Pacific-C01 | SJ-Pacific-C01-PD04 | TRUE | 0 |  |  | 0 |  |  | 0 | RPDU_Operational_Cap | 360 | Local_Capacity_Margin | 360 | Local_Capacity_Margin% | 100% | RPDU_Design_Capacity | 480 | Device_Capacity_Margin | 480 | Device_Capacity_Margin% | 100%
Room PDU | RPDU-R2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD04 | TRUE | 0 |  |  | 0 |  |  | 0 | RPDU_Operational_Cap | 360 | Local_Capacity_Margin | 360 | Local_Capacity_Margin% | 100% | RPDU_Design_Capacity | 480 | Device_Capacity_Margin | 480 | Device_Capacity_Margin% | 100%
Room PDU | RPDU-R3-A | SJ-Pacific-C01 | SJ-Pacific-C01-PD04 | TRUE | 0 |  |  | 0 |  |  | 0 | RPDU_Operational_Cap | 5400 | Local_Capacity_Margin | 5400 | Local_Capacity_Margin% | 100% | RPDU_Design_Capacity | 4000 | Device_Capacity_Margin | 4000 | Device_Capacity_Margin% | 100%
Room PDU | RPDU-R4-A | SJ-Pacific-C01 | SJ-Pacific-C01-PD04 | TRUE | 0 |  |  | 0 |  |  | 0 | RPDU_Operational_Cap | 480 | Local_Capacity_Margin | 480 | Local_Capacity_Margin% | 100% | RPDU_Design_Capacity | 3200 | Device_Capacity_Margin | 3200 | Device_Capacity_Margin% | 100%
Room PDU | RPDU-R5-A | SJ-Pacific-C01 | SJ-Pacific-C01-PD04 | TRUE | 1395 |  |  | 1743.75 |  |  | 24 | RPDU_Operational_Cap | 2880 | Local_Capacity_Margin | 1485 | Local_Capacity_Margin% | 51.56% | RPDU_Design_Capacity | 3200 | Device_Capacity_Margin | 1805 | Device_Capacity_Margin% | 56.41%
Room PDU | RPDU-R3-B | SJ-Pacific-C01 | SJ-Pacific-C01-PD04 | TRUE | 0 |  |  | 0 |  |  | 0 | RPDU_Operational_Cap | 1080 | Local_Capacity_Margin | 1080 | Local_Capacity_Margin% | 100% | RPDU_Design_Capacity | 960 | Device_Capacity_Margin | 960 | Device_Capacity_Margin% | 100%
Room PDU | RPDU-R3R4-B | SJ-Pacific-C01 | SJ-Pacific-C01-PD04 | TRUE | 0 |  |  | 0 |  |  | 0 | RPDU_Operational_Cap | 4800 | Local_Capacity_Margin | 4800 | Local_Capacity_Margin% | 100% | RPDU_Design_Capacity | 4000 | Device_Capacity_Margin | 4000 | Device_Capacity_Margin% | 100%
Room PDU | RPDU-R5-B | SJ-Pacific-C01 | SJ-Pacific-C01-PD04 | TRUE | 1395 |  |  | 1743.75 |  |  | 0 | RPDU_Operational_Cap | 2880 | Local_Capacity_Margin | 1485 | Local_Capacity_Margin% | 51.56% | RPDU_Design_Capacity | 3200 | Device_Capacity_Margin | 1805 | Device_Capacity_Margin% | 56.41%
UPS | UPS-01 | SJ-Pacific-C01 | SJ-Pacific-C01-PD04 | TRUE | 0 |  |  | 0 |  |  | 0 | UPS_Operational_Cap | 720 | Local_Capacity_Margin | 720 | Local_Capacity_Margin% | 100% | UPS_Design_Capacity | 800 | Device_Capacity_Margin | 800 | Device_Capacity_Margin% | 100%
UPS | UPS-02-A | SJ-Pacific-C01 | SJ-Pacific-C01-PD04 | TRUE | 1395 |  |  | 1743.75 |  |  | 24 | UPS_Operational_Cap | 8760 | Local_Capacity_Margin | 7365 | Local_Capacity_Margin% | 84.08% | UPS_Design_Capacity | 9600 | Device_Capacity_Margin | 8205 | Device_Capacity_Margin% | 85.47%
UPS | UPS-02-B | SJ-Pacific-C01 | SJ-Pacific-C01-PD04 | TRUE | 1395 |  |  | 1743.75 |  |  | 0 | UPS_Operational_Cap | 8760 | Local_Capacity_Margin | 7365 | Local_Capacity_Margin% | 84.08% | UPS_Design_Capacity | 9600 | Device_Capacity_Margin | 8205 | Device_Capacity_Margin% | 85.47%
Cooling Distribution | CDIST-A-02 | SJ-Pacific-C01 | SJ-Pacific-C01-PD04 | TRUE |  | 1185.75 |  |  | 1482.1875 |  | 24 |  | 1602 | Local_Capacity_Margin | 1602 | Local_Capacity_Margin% | 100%
Cooling Distribution | CDIST-L-02 | SJ-Pacific-C01 | SJ-Pacific-C01-PD04 | TRUE |  |  | 209.25 |  |  | 261.5625 | 24 |  | 7158 | Local_Capacity_Margin | 7158 | Local_Capacity_Margin% | 100%
Capacity Cell | CC-R1R2 | SJ-Pacific-C01 | SJ-Pacific-C01-PD04 | TRUE | 0 |  |  | 0 |  |  | 0 | Capacity_Envelope | 720 | Cell_Margin | 720 | Cell_Margin% | 100%
Capacity Cell | CC-R3 | SJ-Pacific-C01 | SJ-Pacific-C01-PD04 | TRUE | 0 |  |  | 0 |  |  | 0 | Capacity_Envelope | 5400 | Cell_Margin | 5400 | Cell_Margin% | 100%
Capacity Cell | CC-R4 | SJ-Pacific-C01 | SJ-Pacific-C01-PD04 | TRUE | 0 |  |  | 0 |  |  | 0 | Capacity_Envelope | 480 | Cell_Margin | 480 | Cell_Margin% | 100%
Capacity Cell | CC-R5E | SJ-Pacific-C01 | SJ-Pacific-C01-PD04 | TRUE | 1395 |  |  | 1743.75 |  |  | 24 | Capacity_Envelope | 1440 | Cell_Margin | 45 | Cell_Margin% | 3.125%
Capacity Cell | CC-R5W | SJ-Pacific-C01 | SJ-Pacific-C01-PD04 | TRUE | 0 |  |  | 0 |  |  | 0 | Capacity_Envelope | 1440 | Cell_Margin | 1440 | Cell_Margin% | 100%

## CC
Rack | Capacity Cell | Room Bundle | Room PDU Bundle | UPS Bundle | Rack | Planned Rack Density (kW) | Liquid Loop | Air Zone | RPP-A | RPP-B | Room PDU-A | Room PDU-B | UPS-A | UPS-B
RACK-R3-Z4E-R1-01 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z4E-R1-01 | 45 | LL-R3-E | AIRZONE-R3-E1 | RPP-R3-A1 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z4E-R1-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z4E-R1-02 | 45 | LL-R3-E | AIRZONE-R3-E1 | RPP-R3-A1 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z4E-R1-03 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z4E-R1-03 | 45 | LL-R3-E | AIRZONE-R3-E1 | RPP-R3-A1 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z4E-R1-04 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z4E-R1-04 | 45 | LL-R3-E | AIRZONE-R3-E1 | RPP-R3-A1 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z4E-R1-05 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z4E-R1-05 | 45 | LL-R3-E | AIRZONE-R3-E1 | RPP-R3-A3 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z4E-R1-06 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z4E-R1-06 | 45 | LL-R3-E | AIRZONE-R3-E1 | RPP-R3-A3 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z4E-R1-07 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z4E-R1-07 | 45 | LL-R3-E | AIRZONE-R3-E1 | RPP-R3-A3 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z4E-R1-08 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z4E-R1-08 | 45 | LL-R3-E | AIRZONE-R3-E1 | RPP-R3-A3 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z4E-R1-09 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z4E-R1-09 | 45 | LL-R3-E | AIRZONE-R3-E1 | RPP-R3-A3 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z4E-R1-10 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z4E-R1-10 | 45 | LL-R3-E | AIRZONE-R3-E1 | RPP-R3-A3 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z4E-R1-11 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z4E-R1-11 | 45 | LL-R3-E | AIRZONE-R3-E1 | RPP-R3-A3 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z4E-R1-12 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z4E-R1-12 | 45 | LL-R3-E | AIRZONE-R3-E1 | RPP-R3-A3 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z4E-R2-01 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z4E-R2-01 | 45 | LL-R3-E | AIRZONE-R3-E1 | RPP-R3-A2 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z4E-R2-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z4E-R2-02 | 45 | LL-R3-E | AIRZONE-R3-E1 | RPP-R3-A2 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z4E-R2-03 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z4E-R2-03 | 45 | LL-R3-E | AIRZONE-R3-E1 | RPP-R3-A2 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z4E-R2-04 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z4E-R2-04 | 45 | LL-R3-E | AIRZONE-R3-E1 | RPP-R3-A2 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z4E-R2-05 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z4E-R2-05 | 45 | LL-R3-E | AIRZONE-R3-E1 | RPP-R3-A4 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z4E-R2-06 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z4E-R2-06 | 45 | LL-R3-E | AIRZONE-R3-E1 | RPP-R3-A4 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z4E-R2-07 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z4E-R2-07 | 45 | LL-R3-E | AIRZONE-R3-E1 | RPP-R3-A4 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z4E-R2-08 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z4E-R2-08 | 45 | LL-R3-E | AIRZONE-R3-E1 | RPP-R3-A4 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z4E-R2-09 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z4E-R2-09 | 45 | LL-R3-E | AIRZONE-R3-E1 | RPP-R3-A4 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z4E-R2-10 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z4E-R2-10 | 45 | LL-R3-E | AIRZONE-R3-E1 | RPP-R3-A4 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z4E-R2-11 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z4E-R2-11 | 45 | LL-R3-E | AIRZONE-R3-E1 | RPP-R3-A4 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z4E-R2-12 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z4E-R2-12 | 45 | LL-R3-E | AIRZONE-R3-E1 | RPP-R3-A4 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z5E-R1-01 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z5E-R1-01 | 45 | LL-R3-E | AIRZONE-R3-E1 | RPP-R3-A3 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z5E-R1-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z5E-R1-02 | 45 | LL-R3-E | AIRZONE-R3-E1 | RPP-R3-A4 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z5E-R1-03 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z5E-R1-03 | 45 | LL-R3-E | AIRZONE-R3-E1 | RPP-R3-A3 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z5E-R1-04 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z5E-R1-04 | 45 | LL-R3-E | AIRZONE-R3-E1 | RPP-R3-A4 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z5E-R1-05 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z5E-R1-05 | 45 | LL-R3-E | AIRZONE-R3-E1 | RPP-R3-A3 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z5E-R1-06 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z5E-R1-06 | 45 | LL-R3-E | AIRZONE-R3-E1 | RPP-R3-A4 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z5E-R1-07 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z5E-R1-07 | 45 | LL-R3-E | AIRZONE-R3-E1 | RPP-R3-A3 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z5E-R1-08 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z5E-R1-08 | 45 | LL-R3-E | AIRZONE-R3-E1 | RPP-R3-A4 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z5E-R1-09 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z5E-R1-09 | 45 | LL-R3-E | AIRZONE-R3-E1 | RPP-R3-A3 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z5E-R1-10 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z5E-R1-10 | 45 | LL-R3-E | AIRZONE-R3-E1 | RPP-R3-A4 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z5E-R1-11 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z5E-R1-11 | 45 | LL-R3-E | AIRZONE-R3-E1 | RPP-R3-A3 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z5E-R1-12 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z5E-R1-12 | 45 | LL-R3-E | AIRZONE-R3-E1 | RPP-R3-A4 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z5E-R2-01 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z5E-R2-01 | 45 | LL-R3-E | AIRZONE-R3-E1 | RPP-R3-A3 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z5E-R2-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z5E-R2-02 | 45 | LL-R3-E | AIRZONE-R3-E1 | RPP-R3-A4 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z5E-R2-03 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z5E-R2-03 | 45 | LL-R3-E | AIRZONE-R3-E1 | RPP-R3-A3 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z5E-R2-04 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z5E-R2-04 | 45 | LL-R3-E | AIRZONE-R3-E1 | RPP-R3-A4 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z5E-R2-05 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z5E-R2-05 | 45 | LL-R3-E | AIRZONE-R3-E1 | RPP-R3-A3 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z5E-R2-06 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z5E-R2-06 | 45 | LL-R3-E | AIRZONE-R3-E1 | RPP-R3-A4 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z5E-R2-07 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z5E-R2-07 | 45 | LL-R3-E | AIRZONE-R3-E1 | RPP-R3-A3 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z5E-R2-08 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z5E-R2-08 | 45 | LL-R3-E | AIRZONE-R3-E1 | RPP-R3-A4 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z5E-R2-09 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z5E-R2-09 | 45 | LL-R3-E | AIRZONE-R3-E1 | RPP-R3-A3 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z5E-R2-10 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z5E-R2-10 | 45 | LL-R3-E | AIRZONE-R3-E1 | RPP-R3-A4 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z5E-R2-11 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z5E-R2-11 | 45 | LL-R3-E | AIRZONE-R3-E1 | RPP-R3-A3 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z5E-R2-12 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z5E-R2-12 | 45 | LL-R3-E | AIRZONE-R3-E1 | RPP-R3-A4 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z6E-R1-01 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z6E-R1-01 | 45 | LL-R3-E | AIRZONE-R3-E2 | RPP-R3-A3 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z6E-R1-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z6E-R1-02 | 45 | LL-R3-E | AIRZONE-R3-E2 | RPP-R3-A4 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z6E-R1-03 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z6E-R1-03 | 45 | LL-R3-E | AIRZONE-R3-E2 | RPP-R3-A3 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z6E-R1-04 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z6E-R1-04 | 45 | LL-R3-E | AIRZONE-R3-E2 | RPP-R3-A4 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z6E-R1-05 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z6E-R1-05 | 45 | LL-R3-E | AIRZONE-R3-E2 | RPP-R3-A3 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z6E-R1-06 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z6E-R1-06 | 45 | LL-R3-E | AIRZONE-R3-E2 | RPP-R3-A4 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z6E-R1-07 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z6E-R1-07 | 45 | LL-R3-E | AIRZONE-R3-E2 | RPP-R3-A3 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z6E-R1-08 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z6E-R1-08 | 45 | LL-R3-E | AIRZONE-R3-E2 | RPP-R3-A4 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z6E-R1-09 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z6E-R1-09 | 45 | LL-R3-E | AIRZONE-R3-E2 | RPP-R3-A3 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z6E-R1-10 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z6E-R1-10 | 45 | LL-R3-E | AIRZONE-R3-E2 | RPP-R3-A4 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z6E-R1-11 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z6E-R1-11 | 45 | LL-R3-E | AIRZONE-R3-E2 | RPP-R3-A3 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z6E-R1-12 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z6E-R1-12 | 45 | LL-R3-E | AIRZONE-R3-E2 | RPP-R3-A4 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z6E-R2-01 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z6E-R2-01 | 45 | LL-R3-E | AIRZONE-R3-E2 | RPP-R3-A3 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z6E-R2-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z6E-R2-02 | 45 | LL-R3-E | AIRZONE-R3-E2 | RPP-R3-A4 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z6E-R2-03 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z6E-R2-03 | 45 | LL-R3-E | AIRZONE-R3-E2 | RPP-R3-A3 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z6E-R2-04 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z6E-R2-04 | 45 | LL-R3-E | AIRZONE-R3-E2 | RPP-R3-A4 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z6E-R2-05 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z6E-R2-05 | 45 | LL-R3-E | AIRZONE-R3-E2 | RPP-R3-A3 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z6E-R2-06 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z6E-R2-06 | 45 | LL-R3-E | AIRZONE-R3-E2 | RPP-R3-A4 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z6E-R2-07 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z6E-R2-07 | 45 | LL-R3-E | AIRZONE-R3-E2 | RPP-R3-A3 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z6E-R2-08 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z6E-R2-08 | 45 | LL-R3-E | AIRZONE-R3-E2 | RPP-R3-A4 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z6E-R2-09 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z6E-R2-09 | 45 | LL-R3-E | AIRZONE-R3-E2 | RPP-R3-A3 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z6E-R2-10 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z6E-R2-10 | 45 | LL-R3-E | AIRZONE-R3-E2 | RPP-R3-A4 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z6E-R2-11 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z6E-R2-11 | 45 | LL-R3-E | AIRZONE-R3-E2 | RPP-R3-A3 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z6E-R2-12 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z6E-R2-12 | 45 | LL-R3-E | AIRZONE-R3-E2 | RPP-R3-A4 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z1W-R1-01 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z1W-R1-01 | 30 | LL-R3-W | AIRZONE-R3-W1 | RPP-R3-A1 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z1W-R1-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z1W-R1-02 | 30 | LL-R3-W | AIRZONE-R3-W1 | RPP-R3-A1 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z1W-R1-03 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z1W-R1-03 | 30 | LL-R3-W | AIRZONE-R3-W1 | RPP-R3-A1 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z1W-R1-04 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z1W-R1-04 | 30 | LL-R3-W | AIRZONE-R3-W1 | RPP-R3-A1 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z1W-R1-05 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z1W-R1-05 | 30 | LL-R3-W | AIRZONE-R3-W1 | RPP-R3-A2 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z1W-R1-06 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z1W-R1-06 | 30 | LL-R3-W | AIRZONE-R3-W1 | RPP-R3-A2 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z1W-R1-07 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z1W-R1-07 | 30 | LL-R3-W | AIRZONE-R3-W1 | RPP-R3-A2 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B
RACK-R3-Z1W-R1-08 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z1W-R1-08 | 30 | LL-R3-W | AIRZONE-R3-W1 | RPP-R3-A2 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B
RACK-R3-Z1W-R1-09 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z1W-R1-09 | 30 | LL-R3-W | AIRZONE-R3-W1 | RPP-R3-A1 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B
RACK-R3-Z1W-R1-10 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z1W-R1-10 | 30 | LL-R3-W | AIRZONE-R3-W1 | RPP-R3-A1 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B
RACK-R3-Z1W-R1-11 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z1W-R1-11 | 30 | LL-R3-W | AIRZONE-R3-W1 | RPP-R3-A1 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B
RACK-R3-Z1W-R1-12 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z1W-R1-12 | 30 | LL-R3-W | AIRZONE-R3-W1 | RPP-R3-A1 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B
RACK-R3-Z1W-R2-01 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z1W-R2-01 | 30 | LL-R3-W | AIRZONE-R3-W1 | RPP-R3-A2 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B
RACK-R3-Z1W-R2-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z1W-R2-02 | 30 | LL-R3-W | AIRZONE-R3-W1 | RPP-R3-A2 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B
RACK-R3-Z1W-R2-03 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z1W-R2-03 | 30 | LL-R3-W | AIRZONE-R3-W1 | RPP-R3-A2 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B
RACK-R3-Z1W-R2-04 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z1W-R2-04 | 30 | LL-R3-W | AIRZONE-R3-W1 | RPP-R3-A2 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B
RACK-R3-Z1W-R2-05 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z1W-R2-05 | 30 | LL-R3-W | AIRZONE-R3-W1 | RPP-R3-A1 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B
RACK-R3-Z1W-R2-06 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z1W-R2-06 | 30 | LL-R3-W | AIRZONE-R3-W1 | RPP-R3-A1 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B
RACK-R3-Z1W-R2-07 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z1W-R2-07 | 30 | LL-R3-W | AIRZONE-R3-W1 | RPP-R3-A1 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z1W-R2-08 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z1W-R2-08 | 30 | LL-R3-W | AIRZONE-R3-W1 | RPP-R3-A1 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z1W-R2-09 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z1W-R2-09 | 30 | LL-R3-W | AIRZONE-R3-W1 | RPP-R3-A2 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z1W-R2-10 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z1W-R2-10 | 30 | LL-R3-W | AIRZONE-R3-W1 | RPP-R3-A2 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z1W-R2-11 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z1W-R2-11 | 30 | LL-R3-W | AIRZONE-R3-W1 | RPP-R3-A2 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z1W-R2-12 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z1W-R2-12 | 30 | LL-R3-W | AIRZONE-R3-W1 | RPP-R3-A2 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z2W-R1-01 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z2W-R1-01 | 30 | LL-R3-W | AIRZONE-R3-W1 | RPP-R3-A1 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z2W-R1-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z2W-R1-02 | 30 | LL-R3-W | AIRZONE-R3-W1 | RPP-R3-A1 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z2W-R1-03 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z2W-R1-03 | 30 | LL-R3-W | AIRZONE-R3-W1 | RPP-R3-A1 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z2W-R1-04 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z2W-R1-04 | 30 | LL-R3-W | AIRZONE-R3-W1 | RPP-R3-A1 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z2W-R1-05 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z2W-R1-05 | 30 | LL-R3-W | AIRZONE-R3-W1 | RPP-R3-A2 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z2W-R1-06 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z2W-R1-06 | 30 | LL-R3-W | AIRZONE-R3-W1 | RPP-R3-A2 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z2W-R1-07 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z2W-R1-07 | 30 | LL-R3-W | AIRZONE-R3-W1 | RPP-R3-A2 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B
RACK-R3-Z2W-R1-08 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z2W-R1-08 | 30 | LL-R3-W | AIRZONE-R3-W1 | RPP-R3-A2 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B
RACK-R3-Z2W-R1-09 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z2W-R1-09 | 30 | LL-R3-W | AIRZONE-R3-W1 | RPP-R3-A1 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B
RACK-R3-Z2W-R1-10 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z2W-R1-10 | 30 | LL-R3-W | AIRZONE-R3-W1 | RPP-R3-A1 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B
RACK-R3-Z2W-R1-11 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z2W-R1-11 | 30 | LL-R3-W | AIRZONE-R3-W1 | RPP-R3-A1 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B
RACK-R3-Z2W-R1-12 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z2W-R1-12 | 30 | LL-R3-W | AIRZONE-R3-W1 | RPP-R3-A1 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B
RACK-R3-Z2W-R2-01 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z2W-R2-01 | 30 | LL-R3-W | AIRZONE-R3-W1 | RPP-R3-A2 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B
RACK-R3-Z2W-R2-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z2W-R2-02 | 30 | LL-R3-W | AIRZONE-R3-W1 | RPP-R3-A2 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B
RACK-R3-Z2W-R2-03 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z2W-R2-03 | 30 | LL-R3-W | AIRZONE-R3-W1 | RPP-R3-A2 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B
RACK-R3-Z2W-R2-04 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z2W-R2-04 | 30 | LL-R3-W | AIRZONE-R3-W1 | RPP-R3-A2 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B
RACK-R3-Z2W-R2-05 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z2W-R2-05 | 30 | LL-R3-W | AIRZONE-R3-W1 | RPP-R3-A1 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B
RACK-R3-Z2W-R2-06 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z2W-R2-06 | 30 | LL-R3-W | AIRZONE-R3-W1 | RPP-R3-A1 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B
RACK-R3-Z2W-R2-07 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z2W-R2-07 | 30 | LL-R3-W | AIRZONE-R3-W1 | RPP-R3-A1 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z2W-R2-08 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z2W-R2-08 | 30 | LL-R3-W | AIRZONE-R3-W1 | RPP-R3-A1 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z2W-R2-09 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z2W-R2-09 | 30 | LL-R3-W | AIRZONE-R3-W1 | RPP-R3-A2 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z2W-R2-10 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z2W-R2-10 | 30 | LL-R3-W | AIRZONE-R3-W1 | RPP-R3-A2 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z2W-R2-11 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z2W-R2-11 | 30 | LL-R3-W | AIRZONE-R3-W1 | RPP-R3-A2 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z2W-R2-12 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z2W-R2-12 | 30 | LL-R3-W | AIRZONE-R3-W1 | RPP-R3-A2 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z3W-R1-01 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z3W-R1-01 | 30 | LL-R3-W | AIRZONE-R3-W2 | RPP-R3-A1 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z3W-R1-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z3W-R1-02 | 30 | LL-R3-W | AIRZONE-R3-W2 | RPP-R3-A1 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z3W-R1-03 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z3W-R1-03 | 30 | LL-R3-W | AIRZONE-R3-W2 | RPP-R3-A1 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z3W-R1-04 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z3W-R1-04 | 30 | LL-R3-W | AIRZONE-R3-W2 | RPP-R3-A1 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z3W-R1-05 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z3W-R1-05 | 30 | LL-R3-W | AIRZONE-R3-W2 | RPP-R3-A2 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z3W-R1-06 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z3W-R1-06 | 30 | LL-R3-W | AIRZONE-R3-W2 | RPP-R3-A2 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z3W-R1-07 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z3W-R1-07 | 30 | LL-R3-W | AIRZONE-R3-W2 | RPP-R3-A2 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B
RACK-R3-Z3W-R1-08 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z3W-R1-08 | 30 | LL-R3-W | AIRZONE-R3-W2 | RPP-R3-A2 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B
RACK-R3-Z3W-R1-09 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z3W-R1-09 | 30 | LL-R3-W | AIRZONE-R3-W2 | RPP-R3-A1 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B
RACK-R3-Z3W-R1-10 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z3W-R1-10 | 30 | LL-R3-W | AIRZONE-R3-W2 | RPP-R3-A1 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B
RACK-R3-Z3W-R1-11 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z3W-R1-11 | 30 | LL-R3-W | AIRZONE-R3-W2 | RPP-R3-A1 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B
RACK-R3-Z3W-R1-12 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z3W-R1-12 | 30 | LL-R3-W | AIRZONE-R3-W2 | RPP-R3-A1 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B
RACK-R3-Z3W-R2-01 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z3W-R2-01 | 30 | LL-R3-W | AIRZONE-R3-W2 | RPP-R3-A2 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z3W-R2-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z3W-R2-02 | 30 | LL-R3-W | AIRZONE-R3-W2 | RPP-R3-A2 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z3W-R2-03 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z3W-R2-03 | 30 | LL-R3-W | AIRZONE-R3-W2 | RPP-R3-A2 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z3W-R2-04 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z3W-R2-04 | 30 | LL-R3-W | AIRZONE-R3-W2 | RPP-R3-A2 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z3W-R2-05 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z3W-R2-05 | 30 | LL-R3-W | AIRZONE-R3-W2 | RPP-R3-A1 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z3W-R2-06 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z3W-R2-06 | 30 | LL-R3-W | AIRZONE-R3-W2 | RPP-R3-A1 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R3-Z3W-R2-07 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z3W-R2-07 | 30 | LL-R3-W | AIRZONE-R3-W2 | RPP-R3-A1 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B
RACK-R3-Z3W-R2-08 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z3W-R2-08 | 30 | LL-R3-W | AIRZONE-R3-W2 | RPP-R3-A1 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B
RACK-R3-Z3W-R2-09 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z3W-R2-09 | 30 | LL-R3-W | AIRZONE-R3-W2 | RPP-R3-A2 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B
RACK-R3-Z3W-R2-10 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z3W-R2-10 | 30 | LL-R3-W | AIRZONE-R3-W2 | RPP-R3-A2 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B
RACK-R3-Z3W-R2-11 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z3W-R2-11 | 30 | LL-R3-W | AIRZONE-R3-W2 | RPP-R3-A2 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B
RACK-R3-Z3W-R2-12 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R3-Z3W-R2-12 | 30 | LL-R3-W | AIRZONE-R3-W2 | RPP-R3-A2 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B
RACK-R4-Z1-R1-01 | CC-R4 | BDL-R4 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R4-Z1-R1-01 | 20 | LL-R4 | AIRZONE-R4 | RPP-R4-A5 | RPP-R4-B5 | RPDU-R4-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R4-Z1-R1-02 | CC-R4 | BDL-R4 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R4-Z1-R1-02 | 20 | LL-R4 | AIRZONE-R4 | RPP-R4-A6 | RPP-R4-B6 | RPDU-R4-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R4-Z1-R1-03 | CC-R4 | BDL-R4 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R4-Z1-R1-03 | 20 | LL-R4 | AIRZONE-R4 | RPP-R4-A5 | RPP-R4-B5 | RPDU-R4-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R4-Z1-R1-04 | CC-R4 | BDL-R4 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R4-Z1-R1-04 | 20 | LL-R4 | AIRZONE-R4 | RPP-R4-A6 | RPP-R4-B6 | RPDU-R4-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R4-Z1-R1-05 | CC-R4 | BDL-R4 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R4-Z1-R1-05 | 20 | LL-R4 | AIRZONE-R4 | RPP-R4-A5 | RPP-R4-B5 | RPDU-R4-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R4-Z1-R1-06 | CC-R4 | BDL-R4 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R4-Z1-R1-06 | 20 | LL-R4 | AIRZONE-R4 | RPP-R4-A6 | RPP-R4-B6 | RPDU-R4-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R4-Z1-R1-07 | CC-R4 | BDL-R4 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R4-Z1-R1-07 | 20 | LL-R4 | AIRZONE-R4 | RPP-R4-A5 | RPP-R4-B5 | RPDU-R4-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R4-Z1-R1-08 | CC-R4 | BDL-R4 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R4-Z1-R1-08 | 20 | LL-R4 | AIRZONE-R4 | RPP-R4-A6 | RPP-R4-B6 | RPDU-R4-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R4-Z1-R1-09 | CC-R4 | BDL-R4 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R4-Z1-R1-09 | 20 | LL-R4 | AIRZONE-R4 | RPP-R4-A5 | RPP-R4-B5 | RPDU-R4-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R4-Z1-R1-10 | CC-R4 | BDL-R4 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R4-Z1-R1-10 | 20 | LL-R4 | AIRZONE-R4 | RPP-R4-A6 | RPP-R4-B6 | RPDU-R4-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R4-Z1-R1-11 | CC-R4 | BDL-R4 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R4-Z1-R1-11 | 20 | LL-R4 | AIRZONE-R4 | RPP-R4-A5 | RPP-R4-B5 | RPDU-R4-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R4-Z1-R1-12 | CC-R4 | BDL-R4 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R4-Z1-R1-12 | 20 | LL-R4 | AIRZONE-R4 | RPP-R4-A6 | RPP-R4-B6 | RPDU-R4-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R4-Z1-R2-01 | CC-R4 | BDL-R4 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R4-Z1-R2-01 | 20 | LL-R4 | AIRZONE-R4 | RPP-R4-A5 | RPP-R4-B5 | RPDU-R4-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R4-Z1-R2-02 | CC-R4 | BDL-R4 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R4-Z1-R2-02 | 20 | LL-R4 | AIRZONE-R4 | RPP-R4-A6 | RPP-R4-B6 | RPDU-R4-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R4-Z1-R2-03 | CC-R4 | BDL-R4 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R4-Z1-R2-03 | 20 | LL-R4 | AIRZONE-R4 | RPP-R4-A5 | RPP-R4-B5 | RPDU-R4-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R4-Z1-R2-04 | CC-R4 | BDL-R4 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R4-Z1-R2-04 | 20 | LL-R4 | AIRZONE-R4 | RPP-R4-A6 | RPP-R4-B6 | RPDU-R4-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R4-Z1-R2-05 | CC-R4 | BDL-R4 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R4-Z1-R2-05 | 20 | LL-R4 | AIRZONE-R4 | RPP-R4-A5 | RPP-R4-B5 | RPDU-R4-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R4-Z1-R2-06 | CC-R4 | BDL-R4 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R4-Z1-R2-06 | 20 | LL-R4 | AIRZONE-R4 | RPP-R4-A6 | RPP-R4-B6 | RPDU-R4-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R4-Z1-R2-07 | CC-R4 | BDL-R4 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R4-Z1-R2-07 | 20 | LL-R4 | AIRZONE-R4 | RPP-R4-A5 | RPP-R4-B5 | RPDU-R4-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R4-Z1-R2-08 | CC-R4 | BDL-R4 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R4-Z1-R2-08 | 20 | LL-R4 | AIRZONE-R4 | RPP-R4-A6 | RPP-R4-B6 | RPDU-R4-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R4-Z1-R2-09 | CC-R4 | BDL-R4 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R4-Z1-R2-09 | 20 | LL-R4 | AIRZONE-R4 | RPP-R4-A5 | RPP-R4-B5 | RPDU-R4-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R4-Z1-R2-10 | CC-R4 | BDL-R4 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R4-Z1-R2-10 | 20 | LL-R4 | AIRZONE-R4 | RPP-R4-A6 | RPP-R4-B6 | RPDU-R4-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R4-Z1-R2-11 | CC-R4 | BDL-R4 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R4-Z1-R2-11 | 20 | LL-R4 | AIRZONE-R4 | RPP-R4-A5 | RPP-R4-B5 | RPDU-R4-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R4-Z1-R2-12 | CC-R4 | BDL-R4 | BDL-RPDU-R3R4 | BDL-UPS-02 | RACK-R4-Z1-R2-12 | 20 | LL-R4 | AIRZONE-R4 | RPP-R4-A6 | RPP-R4-B6 | RPDU-R4-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B
RACK-R5-Z1W-R1-01 | CC-R5W | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02 | RACK-R5-Z1W-R1-01 | 60 | LL-R5-W | AIRZONE-R5-W | RPP-R5-A1 | RPP-R5-B1 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B
RACK-R5-Z1W-R1-02 | CC-R5W | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02 | RACK-R5-Z1W-R1-02 | 60 | LL-R5-W | AIRZONE-R5-W | RPP-R5-A1 | RPP-R5-B1 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B
RACK-R5-Z1W-R1-03 | CC-R5W | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02 | RACK-R5-Z1W-R1-03 | 60 | LL-R5-W | AIRZONE-R5-W | RPP-R5-A1 | RPP-R5-B1 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B
RACK-R5-Z1W-R1-04 | CC-R5W | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02 | RACK-R5-Z1W-R1-04 | 60 | LL-R5-W | AIRZONE-R5-W | RPP-R5-A1 | RPP-R5-B1 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B
RACK-R5-Z1W-R1-05 | CC-R5W | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02 | RACK-R5-Z1W-R1-05 | 60 | LL-R5-W | AIRZONE-R5-W | RPP-R5-A1 | RPP-R5-B1 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B
RACK-R5-Z1W-R1-06 | CC-R5W | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02 | RACK-R5-Z1W-R1-06 | 60 | LL-R5-W | AIRZONE-R5-W | RPP-R5-A1 | RPP-R5-B1 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B
RACK-R5-Z1W-R1-07 | CC-R5W | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02 | RACK-R5-Z1W-R1-07 | 60 | LL-R5-W | AIRZONE-R5-W | RPP-R5-A1 | RPP-R5-B1 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B
RACK-R5-Z1W-R1-08 | CC-R5W | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02 | RACK-R5-Z1W-R1-08 | 60 | LL-R5-W | AIRZONE-R5-W | RPP-R5-A1 | RPP-R5-B1 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B
RACK-R5-Z1W-R1-09 | CC-R5W | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02 | RACK-R5-Z1W-R1-09 | 60 | LL-R5-W | AIRZONE-R5-W | RPP-R5-A1 | RPP-R5-B1 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B
RACK-R5-Z1W-R1-10 | CC-R5W | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02 | RACK-R5-Z1W-R1-10 | 60 | LL-R5-W | AIRZONE-R5-W | RPP-R5-A1 | RPP-R5-B1 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B
RACK-R5-Z1W-R1-11 | CC-R5W | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02 | RACK-R5-Z1W-R1-11 | 60 | LL-R5-W | AIRZONE-R5-W | RPP-R5-A1 | RPP-R5-B1 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B
RACK-R5-Z1W-R1-12 | CC-R5W | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02 | RACK-R5-Z1W-R1-12 | 60 | LL-R5-W | AIRZONE-R5-W | RPP-R5-A1 | RPP-R5-B1 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B
RACK-R5-Z1W-R2-01 | CC-R5W | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02 | RACK-R5-Z1W-R2-01 | 60 | LL-R5-W | AIRZONE-R5-W | RPP-R5-A2 | RPP-R5-B2 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B
RACK-R5-Z1W-R2-02 | CC-R5W | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02 | RACK-R5-Z1W-R2-02 | 60 | LL-R5-W | AIRZONE-R5-W | RPP-R5-A2 | RPP-R5-B2 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B
RACK-R5-Z1W-R2-03 | CC-R5W | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02 | RACK-R5-Z1W-R2-03 | 60 | LL-R5-W | AIRZONE-R5-W | RPP-R5-A2 | RPP-R5-B2 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B
RACK-R5-Z1W-R2-04 | CC-R5W | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02 | RACK-R5-Z1W-R2-04 | 60 | LL-R5-W | AIRZONE-R5-W | RPP-R5-A2 | RPP-R5-B2 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B
RACK-R5-Z1W-R2-05 | CC-R5W | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02 | RACK-R5-Z1W-R2-05 | 60 | LL-R5-W | AIRZONE-R5-W | RPP-R5-A2 | RPP-R5-B2 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B
RACK-R5-Z1W-R2-06 | CC-R5W | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02 | RACK-R5-Z1W-R2-06 | 60 | LL-R5-W | AIRZONE-R5-W | RPP-R5-A2 | RPP-R5-B2 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B
RACK-R5-Z1W-R2-07 | CC-R5W | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02 | RACK-R5-Z1W-R2-07 | 60 | LL-R5-W | AIRZONE-R5-W | RPP-R5-A2 | RPP-R5-B2 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B
RACK-R5-Z1W-R2-08 | CC-R5W | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02 | RACK-R5-Z1W-R2-08 | 60 | LL-R5-W | AIRZONE-R5-W | RPP-R5-A2 | RPP-R5-B2 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B
RACK-R5-Z1W-R2-09 | CC-R5W | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02 | RACK-R5-Z1W-R2-09 | 60 | LL-R5-W | AIRZONE-R5-W | RPP-R5-A2 | RPP-R5-B2 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B
RACK-R5-Z1W-R2-10 | CC-R5W | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02 | RACK-R5-Z1W-R2-10 | 60 | LL-R5-W | AIRZONE-R5-W | RPP-R5-A2 | RPP-R5-B2 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B
RACK-R5-Z1W-R2-11 | CC-R5W | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02 | RACK-R5-Z1W-R2-11 | 60 | LL-R5-W | AIRZONE-R5-W | RPP-R5-A2 | RPP-R5-B2 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B
RACK-R5-Z1W-R2-12 | CC-R5W | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02 | RACK-R5-Z1W-R2-12 | 60 | LL-R5-W | AIRZONE-R5-W | RPP-R5-A2 | RPP-R5-B2 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B
RACK-R5-Z2E-R1-01 | CC-R5E | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02 | RACK-R5-Z2E-R1-01 | 60 | LL-R5-E | AIRZONE-R5-E | RPP-R5-A3 | RPP-R5-B3 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B
RACK-R5-Z2E-R1-02 | CC-R5E | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02 | RACK-R5-Z2E-R1-02 | 60 | LL-R5-E | AIRZONE-R5-E | RPP-R5-A3 | RPP-R5-B3 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B
RACK-R5-Z2E-R1-03 | CC-R5E | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02 | RACK-R5-Z2E-R1-03 | 60 | LL-R5-E | AIRZONE-R5-E | RPP-R5-A3 | RPP-R5-B3 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B
RACK-R5-Z2E-R1-04 | CC-R5E | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02 | RACK-R5-Z2E-R1-04 | 60 | LL-R5-E | AIRZONE-R5-E | RPP-R5-A3 | RPP-R5-B3 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B
RACK-R5-Z2E-R1-05 | CC-R5E | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02 | RACK-R5-Z2E-R1-05 | 60 | LL-R5-E | AIRZONE-R5-E | RPP-R5-A3 | RPP-R5-B3 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B
RACK-R5-Z2E-R1-06 | CC-R5E | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02 | RACK-R5-Z2E-R1-06 | 60 | LL-R5-E | AIRZONE-R5-E | RPP-R5-A3 | RPP-R5-B3 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B
RACK-R5-Z2E-R1-07 | CC-R5E | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02 | RACK-R5-Z2E-R1-07 | 60 | LL-R5-E | AIRZONE-R5-E | RPP-R5-A3 | RPP-R5-B3 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B
RACK-R5-Z2E-R1-08 | CC-R5E | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02 | RACK-R5-Z2E-R1-08 | 60 | LL-R5-E | AIRZONE-R5-E | RPP-R5-A3 | RPP-R5-B3 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B
RACK-R5-Z2E-R1-09 | CC-R5E | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02 | RACK-R5-Z2E-R1-09 | 60 | LL-R5-E | AIRZONE-R5-E | RPP-R5-A3 | RPP-R5-B3 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B
RACK-R5-Z2E-R1-10 | CC-R5E | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02 | RACK-R5-Z2E-R1-10 | 60 | LL-R5-E | AIRZONE-R5-E | RPP-R5-A3 | RPP-R5-B3 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B
RACK-R5-Z2E-R1-11 | CC-R5E | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02 | RACK-R5-Z2E-R1-11 | 60 | LL-R5-E | AIRZONE-R5-E | RPP-R5-A3 | RPP-R5-B3 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B
RACK-R5-Z2E-R1-12 | CC-R5E | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02 | RACK-R5-Z2E-R1-12 | 60 | LL-R5-E | AIRZONE-R5-E | RPP-R5-A3 | RPP-R5-B3 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B
RACK-R5-Z2E-R2-01 | CC-R5E | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02 | RACK-R5-Z2E-R2-01 | 60 | LL-R5-E | AIRZONE-R5-E | RPP-R5-A4 | RPP-R5-B4 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B
RACK-R5-Z2E-R2-02 | CC-R5E | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02 | RACK-R5-Z2E-R2-02 | 60 | LL-R5-E | AIRZONE-R5-E | RPP-R5-A4 | RPP-R5-B4 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B
RACK-R5-Z2E-R2-03 | CC-R5E | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02 | RACK-R5-Z2E-R2-03 | 60 | LL-R5-E | AIRZONE-R5-E | RPP-R5-A4 | RPP-R5-B4 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B
RACK-R5-Z2E-R2-04 | CC-R5E | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02 | RACK-R5-Z2E-R2-04 | 60 | LL-R5-E | AIRZONE-R5-E | RPP-R5-A4 | RPP-R5-B4 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B
RACK-R5-Z2E-R2-05 | CC-R5E | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02 | RACK-R5-Z2E-R2-05 | 60 | LL-R5-E | AIRZONE-R5-E | RPP-R5-A4 | RPP-R5-B4 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B
RACK-R5-Z2E-R2-06 | CC-R5E | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02 | RACK-R5-Z2E-R2-06 | 60 | LL-R5-E | AIRZONE-R5-E | RPP-R5-A4 | RPP-R5-B4 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B
RACK-R5-Z2E-R2-07 | CC-R5E | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02 | RACK-R5-Z2E-R2-07 | 60 | LL-R5-E | AIRZONE-R5-E | RPP-R5-A4 | RPP-R5-B4 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B
RACK-R5-Z2E-R2-08 | CC-R5E | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02 | RACK-R5-Z2E-R2-08 | 60 | LL-R5-E | AIRZONE-R5-E | RPP-R5-A4 | RPP-R5-B4 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B
RACK-R5-Z2E-R2-09 | CC-R5E | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02 | RACK-R5-Z2E-R2-09 | 60 | LL-R5-E | AIRZONE-R5-E | RPP-R5-A4 | RPP-R5-B4 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B
RACK-R5-Z2E-R2-10 | CC-R5E | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02 | RACK-R5-Z2E-R2-10 | 60 | LL-R5-E | AIRZONE-R5-E | RPP-R5-A4 | RPP-R5-B4 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B
RACK-R5-Z2E-R2-11 | CC-R5E | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02 | RACK-R5-Z2E-R2-11 | 60 | LL-R5-E | AIRZONE-R5-E | RPP-R5-A4 | RPP-R5-B4 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B
RACK-R5-Z2E-R2-12 | CC-R5E | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02 | RACK-R5-Z2E-R2-12 | 60 | LL-R5-E | AIRZONE-R5-E | RPP-R5-A4 | RPP-R5-B4 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B
RACK-R1-Z1-R1-01 | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01 | RACK-R1-Z1-R1-01 | 15 | LL-R1 | AIRZONE-R1 | RPP-R1-1 |  | RPDU-R1 |  | UPS-01
RACK-R1-Z1-R1-02 | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01 | RACK-R1-Z1-R1-02 | 15 | LL-R1 | AIRZONE-R1 | RPP-R1-2 |  | RPDU-R1 |  | UPS-01
RACK-R1-Z1-R1-03 | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01 | RACK-R1-Z1-R1-03 | 15 | LL-R1 | AIRZONE-R1 | RPP-R2-1 |  | RPDU-R2 |  | UPS-01
RACK-R1-Z1-R1-04 | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01 | RACK-R1-Z1-R1-04 | 15 | LL-R1 | AIRZONE-R1 | RPP-R2-2 |  | RPDU-R2 |  | UPS-01
RACK-R1-Z1-R1-05 | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01 | RACK-R1-Z1-R1-05 | 15 | LL-R1 | AIRZONE-R1 | RPP-R1-1 |  | RPDU-R1 |  | UPS-01
RACK-R1-Z1-R1-06 | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01 | RACK-R1-Z1-R1-06 | 15 | LL-R1 | AIRZONE-R1 | RPP-R1-2 |  | RPDU-R1 |  | UPS-01
RACK-R1-Z1-R2-01 | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01 | RACK-R1-Z1-R2-01 | 15 | LL-R1 | AIRZONE-R1 | RPP-R2-1 |  | RPDU-R2 |  | UPS-01
RACK-R1-Z1-R2-02 | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01 | RACK-R1-Z1-R2-02 | 15 | LL-R1 | AIRZONE-R1 | RPP-R2-2 |  | RPDU-R2 |  | UPS-01
RACK-R1-Z1-R2-03 | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01 | RACK-R1-Z1-R2-03 | 15 | LL-R1 | AIRZONE-R1 | RPP-R1-1 |  | RPDU-R1 |  | UPS-01
RACK-R1-Z1-R2-04 | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01 | RACK-R1-Z1-R2-04 | 15 | LL-R1 | AIRZONE-R1 | RPP-R1-2 |  | RPDU-R1 |  | UPS-01
RACK-R1-Z1-R2-05 | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01 | RACK-R1-Z1-R2-05 | 15 | LL-R1 | AIRZONE-R1 | RPP-R2-1 |  | RPDU-R2 |  | UPS-01
RACK-R1-Z1-R2-06 | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01 | RACK-R1-Z1-R2-06 | 15 | LL-R1 | AIRZONE-R1 | RPP-R2-2 |  | RPDU-R2 |  | UPS-01
RACK-R1-Z2-R1-01 | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01 | RACK-R1-Z2-R1-01 | 15 | LL-R1 | AIRZONE-R1 | RPP-R1-1 |  | RPDU-R1 |  | UPS-01
RACK-R1-Z2-R1-02 | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01 | RACK-R1-Z2-R1-02 | 15 | LL-R1 | AIRZONE-R1 | RPP-R1-2 |  | RPDU-R1 |  | UPS-01
RACK-R1-Z2-R1-03 | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01 | RACK-R1-Z2-R1-03 | 15 | LL-R1 | AIRZONE-R1 | RPP-R2-1 |  | RPDU-R2 |  | UPS-01
RACK-R1-Z2-R1-04 | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01 | RACK-R1-Z2-R1-04 | 15 | LL-R1 | AIRZONE-R1 | RPP-R2-2 |  | RPDU-R2 |  | UPS-01
RACK-R1-Z2-R1-05 | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01 | RACK-R1-Z2-R1-05 | 15 | LL-R1 | AIRZONE-R1 | RPP-R1-1 |  | RPDU-R1 |  | UPS-01
RACK-R1-Z2-R1-06 | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01 | RACK-R1-Z2-R1-06 | 15 | LL-R1 | AIRZONE-R1 | RPP-R1-2 |  | RPDU-R1 |  | UPS-01
RACK-R1-Z2-R2-01 | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01 | RACK-R1-Z2-R2-01 | 15 | LL-R1 | AIRZONE-R1 | RPP-R2-1 |  | RPDU-R2 |  | UPS-01
RACK-R1-Z2-R2-02 | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01 | RACK-R1-Z2-R2-02 | 15 | LL-R1 | AIRZONE-R1 | RPP-R2-2 |  | RPDU-R2 |  | UPS-01
RACK-R1-Z2-R2-03 | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01 | RACK-R1-Z2-R2-03 | 15 | LL-R1 | AIRZONE-R1 | RPP-R1-1 |  | RPDU-R1 |  | UPS-01
RACK-R1-Z2-R2-04 | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01 | RACK-R1-Z2-R2-04 | 15 | LL-R1 | AIRZONE-R1 | RPP-R1-2 |  | RPDU-R1 |  | UPS-01
RACK-R1-Z2-R2-05 | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01 | RACK-R1-Z2-R2-05 | 15 | LL-R1 | AIRZONE-R1 | RPP-R2-1 |  | RPDU-R2 |  | UPS-01
RACK-R1-Z2-R2-06 | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01 | RACK-R1-Z2-R2-06 | 15 | LL-R1 | AIRZONE-R1 | RPP-R2-2 |  | RPDU-R2 |  | UPS-01
RACK-R2-Z1-R1-01 | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01 | RACK-R2-Z1-R1-01 | 15 | LL-R2 | AIRZONE-R2 | RPP-R1-1 |  | RPDU-R1 |  | UPS-01
RACK-R2-Z1-R1-02 | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01 | RACK-R2-Z1-R1-02 | 15 | LL-R2 | AIRZONE-R2 | RPP-R1-2 |  | RPDU-R1 |  | UPS-01
RACK-R2-Z1-R1-03 | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01 | RACK-R2-Z1-R1-03 | 15 | LL-R2 | AIRZONE-R2 | RPP-R2-1 |  | RPDU-R2 |  | UPS-01
RACK-R2-Z1-R1-04 | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01 | RACK-R2-Z1-R1-04 | 15 | LL-R2 | AIRZONE-R2 | RPP-R2-2 |  | RPDU-R2 |  | UPS-01
RACK-R2-Z1-R1-05 | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01 | RACK-R2-Z1-R1-05 | 15 | LL-R2 | AIRZONE-R2 | RPP-R1-1 |  | RPDU-R1 |  | UPS-01
RACK-R2-Z1-R1-06 | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01 | RACK-R2-Z1-R1-06 | 15 | LL-R2 | AIRZONE-R2 | RPP-R1-2 |  | RPDU-R1 |  | UPS-01
RACK-R2-Z1-R2-01 | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01 | RACK-R2-Z1-R2-01 | 15 | LL-R2 | AIRZONE-R2 | RPP-R2-1 |  | RPDU-R2 |  | UPS-01
RACK-R2-Z1-R2-02 | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01 | RACK-R2-Z1-R2-02 | 15 | LL-R2 | AIRZONE-R2 | RPP-R2-2 |  | RPDU-R2 |  | UPS-01
RACK-R2-Z1-R2-03 | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01 | RACK-R2-Z1-R2-03 | 15 | LL-R2 | AIRZONE-R2 | RPP-R1-1 |  | RPDU-R1 |  | UPS-01
RACK-R2-Z1-R2-04 | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01 | RACK-R2-Z1-R2-04 | 15 | LL-R2 | AIRZONE-R2 | RPP-R1-2 |  | RPDU-R1 |  | UPS-01
RACK-R2-Z1-R2-05 | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01 | RACK-R2-Z1-R2-05 | 15 | LL-R2 | AIRZONE-R2 | RPP-R2-1 |  | RPDU-R2 |  | UPS-01
RACK-R2-Z1-R2-06 | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01 | RACK-R2-Z1-R2-06 | 15 | LL-R2 | AIRZONE-R2 | RPP-R2-2 |  | RPDU-R2 |  | UPS-01
RACK-R2-Z2-R1-01 | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01 | RACK-R2-Z2-R1-01 | 15 | LL-R2 | AIRZONE-R2 | RPP-R1-1 |  | RPDU-R1 |  | UPS-01
RACK-R2-Z2-R1-02 | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01 | RACK-R2-Z2-R1-02 | 15 | LL-R2 | AIRZONE-R2 | RPP-R1-2 |  | RPDU-R1 |  | UPS-01
RACK-R2-Z2-R1-03 | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01 | RACK-R2-Z2-R1-03 | 15 | LL-R2 | AIRZONE-R2 | RPP-R2-1 |  | RPDU-R2 |  | UPS-01
RACK-R2-Z2-R1-04 | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01 | RACK-R2-Z2-R1-04 | 15 | LL-R2 | AIRZONE-R2 | RPP-R2-2 |  | RPDU-R2 |  | UPS-01
RACK-R2-Z2-R1-05 | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01 | RACK-R2-Z2-R1-05 | 15 | LL-R2 | AIRZONE-R2 | RPP-R1-1 |  | RPDU-R1 |  | UPS-01
RACK-R2-Z2-R1-06 | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01 | RACK-R2-Z2-R1-06 | 15 | LL-R2 | AIRZONE-R2 | RPP-R1-2 |  | RPDU-R1 |  | UPS-01
RACK-R2-Z2-R2-01 | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01 | RACK-R2-Z2-R2-01 | 15 | LL-R2 | AIRZONE-R2 | RPP-R2-1 |  | RPDU-R2 |  | UPS-01
RACK-R2-Z2-R2-02 | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01 | RACK-R2-Z2-R2-02 | 15 | LL-R2 | AIRZONE-R2 | RPP-R2-2 |  | RPDU-R2 |  | UPS-01
RACK-R2-Z2-R2-03 | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01 | RACK-R2-Z2-R2-03 | 15 | LL-R2 | AIRZONE-R2 | RPP-R1-1 |  | RPDU-R1 |  | UPS-01
RACK-R2-Z2-R2-04 | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01 | RACK-R2-Z2-R2-04 | 15 | LL-R2 | AIRZONE-R2 | RPP-R1-2 |  | RPDU-R1 |  | UPS-01
RACK-R2-Z2-R2-05 | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01 | RACK-R2-Z2-R2-05 | 15 | LL-R2 | AIRZONE-R2 | RPP-R2-1 |  | RPDU-R2 |  | UPS-01
RACK-R2-Z2-R2-06 | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01 | RACK-R2-Z2-R2-06 | 15 | LL-R2 | AIRZONE-R2 | RPP-R2-2 |  | RPDU-R2 |  | UPS-01

## Cooling-Rack
Rack | Planned Rack Density (Rack_Circuit_Capacity_(design)) | Liquid Loop | Rack_LiquidCool_Fraction | Liquid Cooling Load | CDU | Air Heat Load | Air Zone
RACK-R3-Z1W-R1-01 | 30 | LL-R3-W | 75% | 22.5 | CDU-R3-W | 7.5 | AIRZONE-R3-W1
RACK-R3-Z1W-R1-02 | 30 | LL-R3-W | 75% | 22.5 | CDU-R3-W | 7.5 | AIRZONE-R3-W1
RACK-R3-Z1W-R1-03 | 30 | LL-R3-W | 75% | 22.5 | CDU-R3-W | 7.5 | AIRZONE-R3-W1
RACK-R3-Z1W-R1-04 | 30 | LL-R3-W | 75% | 22.5 | CDU-R3-W | 7.5 | AIRZONE-R3-W1
RACK-R3-Z1W-R1-05 | 30 | LL-R3-W | 75% | 22.5 | CDU-R3-W | 7.5 | AIRZONE-R3-W1
RACK-R3-Z1W-R1-06 | 30 | LL-R3-W | 75% | 22.5 | CDU-R3-W | 7.5 | AIRZONE-R3-W1
RACK-R3-Z1W-R1-07 | 30 | LL-R3-W | 75% | 22.5 | CDU-R3-W | 7.5 | AIRZONE-R3-W1
RACK-R3-Z1W-R1-08 | 30 | LL-R3-W | 75% | 22.5 | CDU-R3-W | 7.5 | AIRZONE-R3-W1
RACK-R3-Z1W-R1-09 | 30 | LL-R3-W | 75% | 22.5 | CDU-R3-W | 7.5 | AIRZONE-R3-W1
RACK-R3-Z1W-R1-10 | 30 | LL-R3-W | 75% | 22.5 | CDU-R3-W | 7.5 | AIRZONE-R3-W1
RACK-R3-Z1W-R1-11 | 30 | LL-R3-W | 75% | 22.5 | CDU-R3-W | 7.5 | AIRZONE-R3-W1
RACK-R3-Z1W-R1-12 | 30 | LL-R3-W | 75% | 22.5 | CDU-R3-W | 7.5 | AIRZONE-R3-W1
RACK-R3-Z1W-R2-01 | 30 | LL-R3-W | 75% | 22.5 | CDU-R3-W | 7.5 | AIRZONE-R3-W1
RACK-R3-Z1W-R2-02 | 30 | LL-R3-W | 75% | 22.5 | CDU-R3-W | 7.5 | AIRZONE-R3-W1
RACK-R3-Z1W-R2-03 | 30 | LL-R3-W | 75% | 22.5 | CDU-R3-W | 7.5 | AIRZONE-R3-W1
RACK-R3-Z1W-R2-04 | 30 | LL-R3-W | 75% | 22.5 | CDU-R3-W | 7.5 | AIRZONE-R3-W1
RACK-R3-Z1W-R2-05 | 30 | LL-R3-W | 75% | 22.5 | CDU-R3-W | 7.5 | AIRZONE-R3-W1
RACK-R3-Z1W-R2-06 | 30 | LL-R3-W | 75% | 22.5 | CDU-R3-W | 7.5 | AIRZONE-R3-W1
RACK-R3-Z1W-R2-07 | 30 | LL-R3-W | 75% | 22.5 | CDU-R3-W | 7.5 | AIRZONE-R3-W1
RACK-R3-Z1W-R2-08 | 30 | LL-R3-W | 75% | 22.5 | CDU-R3-W | 7.5 | AIRZONE-R3-W1
RACK-R3-Z1W-R2-09 | 30 | LL-R3-W | 75% | 22.5 | CDU-R3-W | 7.5 | AIRZONE-R3-W1
RACK-R3-Z1W-R2-10 | 30 | LL-R3-W | 75% | 22.5 | CDU-R3-W | 7.5 | AIRZONE-R3-W1
RACK-R3-Z1W-R2-11 | 30 | LL-R3-W | 75% | 22.5 | CDU-R3-W | 7.5 | AIRZONE-R3-W1
RACK-R3-Z1W-R2-12 | 30 | LL-R3-W | 75% | 22.5 | CDU-R3-W | 7.5 | AIRZONE-R3-W1
RACK-R3-Z2W-R1-01 | 30 | LL-R3-W | 75% | 22.5 | CDU-R3-W | 7.5 | AIRZONE-R3-W1
RACK-R3-Z2W-R1-02 | 30 | LL-R3-W | 75% | 22.5 | CDU-R3-W | 7.5 | AIRZONE-R3-W1
RACK-R3-Z2W-R1-03 | 30 | LL-R3-W | 75% | 22.5 | CDU-R3-W | 7.5 | AIRZONE-R3-W1
RACK-R3-Z2W-R1-04 | 30 | LL-R3-W | 75% | 22.5 | CDU-R3-W | 7.5 | AIRZONE-R3-W1
RACK-R3-Z2W-R1-05 | 30 | LL-R3-W | 75% | 22.5 | CDU-R3-W | 7.5 | AIRZONE-R3-W1
RACK-R3-Z2W-R1-06 | 30 | LL-R3-W | 75% | 22.5 | CDU-R3-W | 7.5 | AIRZONE-R3-W1
RACK-R3-Z2W-R1-07 | 30 | LL-R3-W | 75% | 22.5 | CDU-R3-W | 7.5 | AIRZONE-R3-W1
RACK-R3-Z2W-R1-08 | 30 | LL-R3-W | 75% | 22.5 | CDU-R3-W | 7.5 | AIRZONE-R3-W1
RACK-R3-Z2W-R1-09 | 30 | LL-R3-W | 75% | 22.5 | CDU-R3-W | 7.5 | AIRZONE-R3-W1
RACK-R3-Z2W-R1-10 | 30 | LL-R3-W | 75% | 22.5 | CDU-R3-W | 7.5 | AIRZONE-R3-W1
RACK-R3-Z2W-R1-11 | 30 | LL-R3-W | 75% | 22.5 | CDU-R3-W | 7.5 | AIRZONE-R3-W1
RACK-R3-Z2W-R1-12 | 30 | LL-R3-W | 75% | 22.5 | CDU-R3-W | 7.5 | AIRZONE-R3-W1
RACK-R3-Z2W-R2-01 | 30 | LL-R3-W | 75% | 22.5 | CDU-R3-W | 7.5 | AIRZONE-R3-W1
RACK-R3-Z2W-R2-02 | 30 | LL-R3-W | 75% | 22.5 | CDU-R3-W | 7.5 | AIRZONE-R3-W1
RACK-R3-Z2W-R2-03 | 30 | LL-R3-W | 75% | 22.5 | CDU-R3-W | 7.5 | AIRZONE-R3-W1
RACK-R3-Z2W-R2-04 | 30 | LL-R3-W | 75% | 22.5 | CDU-R3-W | 7.5 | AIRZONE-R3-W1
RACK-R3-Z2W-R2-05 | 30 | LL-R3-W | 75% | 22.5 | CDU-R3-W | 7.5 | AIRZONE-R3-W1
RACK-R3-Z2W-R2-06 | 30 | LL-R3-W | 75% | 22.5 | CDU-R3-W | 7.5 | AIRZONE-R3-W1
RACK-R3-Z2W-R2-07 | 30 | LL-R3-W | 75% | 22.5 | CDU-R3-W | 7.5 | AIRZONE-R3-W1
RACK-R3-Z2W-R2-08 | 30 | LL-R3-W | 75% | 22.5 | CDU-R3-W | 7.5 | AIRZONE-R3-W1
RACK-R3-Z2W-R2-09 | 30 | LL-R3-W | 75% | 22.5 | CDU-R3-W | 7.5 | AIRZONE-R3-W1
RACK-R3-Z2W-R2-10 | 30 | LL-R3-W | 75% | 22.5 | CDU-R3-W | 7.5 | AIRZONE-R3-W1
RACK-R3-Z2W-R2-11 | 30 | LL-R3-W | 75% | 22.5 | CDU-R3-W | 7.5 | AIRZONE-R3-W1
RACK-R3-Z2W-R2-12 | 30 | LL-R3-W | 75% | 22.5 | CDU-R3-W | 7.5 | AIRZONE-R3-W1
RACK-R3-Z3W-R1-01 | 30 | LL-R3-W | 75% | 22.5 | CDU-R3-W | 7.5 | AIRZONE-R3-W2
RACK-R3-Z3W-R1-02 | 30 | LL-R3-W | 75% | 22.5 | CDU-R3-W | 7.5 | AIRZONE-R3-W2
RACK-R3-Z3W-R1-03 | 30 | LL-R3-W | 75% | 22.5 | CDU-R3-W | 7.5 | AIRZONE-R3-W2
RACK-R3-Z3W-R1-04 | 30 | LL-R3-W | 75% | 22.5 | CDU-R3-W | 7.5 | AIRZONE-R3-W2
RACK-R3-Z3W-R1-05 | 30 | LL-R3-W | 75% | 22.5 | CDU-R3-W | 7.5 | AIRZONE-R3-W2
RACK-R3-Z3W-R1-06 | 30 | LL-R3-W | 75% | 22.5 | CDU-R3-W | 7.5 | AIRZONE-R3-W2
RACK-R3-Z3W-R1-07 | 30 | LL-R3-W | 75% | 22.5 | CDU-R3-W | 7.5 | AIRZONE-R3-W2
RACK-R3-Z3W-R1-08 | 30 | LL-R3-W | 75% | 22.5 | CDU-R3-W | 7.5 | AIRZONE-R3-W2
RACK-R3-Z3W-R1-09 | 30 | LL-R3-W | 75% | 22.5 | CDU-R3-W | 7.5 | AIRZONE-R3-W2
RACK-R3-Z3W-R1-10 | 30 | LL-R3-W | 75% | 22.5 | CDU-R3-W | 7.5 | AIRZONE-R3-W2
RACK-R3-Z3W-R1-11 | 30 | LL-R3-W | 75% | 22.5 | CDU-R3-W | 7.5 | AIRZONE-R3-W2
RACK-R3-Z3W-R1-12 | 30 | LL-R3-W | 75% | 22.5 | CDU-R3-W | 7.5 | AIRZONE-R3-W2
RACK-R3-Z3W-R2-01 | 30 | LL-R3-W | 75% | 22.5 | CDU-R3-W | 7.5 | AIRZONE-R3-W2
RACK-R3-Z3W-R2-02 | 30 | LL-R3-W | 75% | 22.5 | CDU-R3-W | 7.5 | AIRZONE-R3-W2
RACK-R3-Z3W-R2-03 | 30 | LL-R3-W | 75% | 22.5 | CDU-R3-W | 7.5 | AIRZONE-R3-W2
RACK-R3-Z3W-R2-04 | 30 | LL-R3-W | 75% | 22.5 | CDU-R3-W | 7.5 | AIRZONE-R3-W2
RACK-R3-Z3W-R2-05 | 30 | LL-R3-W | 75% | 22.5 | CDU-R3-W | 7.5 | AIRZONE-R3-W2
RACK-R3-Z3W-R2-06 | 30 | LL-R3-W | 75% | 22.5 | CDU-R3-W | 7.5 | AIRZONE-R3-W2
RACK-R3-Z3W-R2-07 | 30 | LL-R3-W | 75% | 22.5 | CDU-R3-W | 7.5 | AIRZONE-R3-W2
RACK-R3-Z3W-R2-08 | 30 | LL-R3-W | 75% | 22.5 | CDU-R3-W | 7.5 | AIRZONE-R3-W2
RACK-R3-Z3W-R2-09 | 30 | LL-R3-W | 75% | 22.5 | CDU-R3-W | 7.5 | AIRZONE-R3-W2
RACK-R3-Z3W-R2-10 | 30 | LL-R3-W | 75% | 22.5 | CDU-R3-W | 7.5 | AIRZONE-R3-W2
RACK-R3-Z3W-R2-11 | 30 | LL-R3-W | 75% | 22.5 | CDU-R3-W | 7.5 | AIRZONE-R3-W2
RACK-R3-Z3W-R2-12 | 30 | LL-R3-W | 75% | 22.5 | CDU-R3-W | 7.5 | AIRZONE-R3-W2
RACK-R3-Z4E-R1-01 | 45 | LL-R3-E | 85% | 38.25 | CDU-R3-E | 6.75 | AIRZONE-R3-E1
RACK-R3-Z4E-R1-02 | 45 | LL-R3-E | 85% | 38.25 | CDU-R3-E | 6.75 | AIRZONE-R3-E1
RACK-R3-Z4E-R1-03 | 45 | LL-R3-E | 85% | 38.25 | CDU-R3-E | 6.75 | AIRZONE-R3-E1
RACK-R3-Z4E-R1-04 | 45 | LL-R3-E | 85% | 38.25 | CDU-R3-E | 6.75 | AIRZONE-R3-E1
RACK-R3-Z4E-R1-05 | 45 | LL-R3-E | 85% | 38.25 | CDU-R3-E | 6.75 | AIRZONE-R3-E1
RACK-R3-Z4E-R1-06 | 45 | LL-R3-E | 85% | 38.25 | CDU-R3-E | 6.75 | AIRZONE-R3-E1
RACK-R3-Z4E-R1-07 | 45 | LL-R3-E | 85% | 38.25 | CDU-R3-E | 6.75 | AIRZONE-R3-E1
RACK-R3-Z4E-R1-08 | 45 | LL-R3-E | 85% | 38.25 | CDU-R3-E | 6.75 | AIRZONE-R3-E1
RACK-R3-Z4E-R1-09 | 45 | LL-R3-E | 85% | 38.25 | CDU-R3-E | 6.75 | AIRZONE-R3-E1
RACK-R3-Z4E-R1-10 | 45 | LL-R3-E | 85% | 38.25 | CDU-R3-E | 6.75 | AIRZONE-R3-E1
RACK-R3-Z4E-R1-11 | 45 | LL-R3-E | 85% | 38.25 | CDU-R3-E | 6.75 | AIRZONE-R3-E1
RACK-R3-Z4E-R1-12 | 45 | LL-R3-E | 85% | 38.25 | CDU-R3-E | 6.75 | AIRZONE-R3-E1
RACK-R3-Z4E-R2-01 | 45 | LL-R3-E | 85% | 38.25 | CDU-R3-E | 6.75 | AIRZONE-R3-E1
RACK-R3-Z4E-R2-02 | 45 | LL-R3-E | 85% | 38.25 | CDU-R3-E | 6.75 | AIRZONE-R3-E1
RACK-R3-Z4E-R2-03 | 45 | LL-R3-E | 85% | 38.25 | CDU-R3-E | 6.75 | AIRZONE-R3-E1
RACK-R3-Z4E-R2-04 | 45 | LL-R3-E | 85% | 38.25 | CDU-R3-E | 6.75 | AIRZONE-R3-E1
RACK-R3-Z4E-R2-05 | 45 | LL-R3-E | 85% | 38.25 | CDU-R3-E | 6.75 | AIRZONE-R3-E1
RACK-R3-Z4E-R2-06 | 45 | LL-R3-E | 85% | 38.25 | CDU-R3-E | 6.75 | AIRZONE-R3-E1
RACK-R3-Z4E-R2-07 | 45 | LL-R3-E | 85% | 38.25 | CDU-R3-E | 6.75 | AIRZONE-R3-E1
RACK-R3-Z4E-R2-08 | 45 | LL-R3-E | 85% | 38.25 | CDU-R3-E | 6.75 | AIRZONE-R3-E1
RACK-R3-Z4E-R2-09 | 45 | LL-R3-E | 85% | 38.25 | CDU-R3-E | 6.75 | AIRZONE-R3-E1
RACK-R3-Z4E-R2-10 | 45 | LL-R3-E | 85% | 38.25 | CDU-R3-E | 6.75 | AIRZONE-R3-E1
RACK-R3-Z4E-R2-11 | 45 | LL-R3-E | 85% | 38.25 | CDU-R3-E | 6.75 | AIRZONE-R3-E1
RACK-R3-Z4E-R2-12 | 45 | LL-R3-E | 85% | 38.25 | CDU-R3-E | 6.75 | AIRZONE-R3-E1
RACK-R3-Z5E-R1-01 | 45 | LL-R3-E | 85% | 38.25 | CDU-R3-E | 6.75 | AIRZONE-R3-E1
RACK-R3-Z5E-R1-02 | 45 | LL-R3-E | 85% | 38.25 | CDU-R3-E | 6.75 | AIRZONE-R3-E1
RACK-R3-Z5E-R1-03 | 45 | LL-R3-E | 85% | 38.25 | CDU-R3-E | 6.75 | AIRZONE-R3-E1
RACK-R3-Z5E-R1-04 | 45 | LL-R3-E | 85% | 38.25 | CDU-R3-E | 6.75 | AIRZONE-R3-E1
RACK-R3-Z5E-R1-05 | 45 | LL-R3-E | 85% | 38.25 | CDU-R3-E | 6.75 | AIRZONE-R3-E1
RACK-R3-Z5E-R1-06 | 45 | LL-R3-E | 85% | 38.25 | CDU-R3-E | 6.75 | AIRZONE-R3-E1
RACK-R3-Z5E-R1-07 | 45 | LL-R3-E | 85% | 38.25 | CDU-R3-E | 6.75 | AIRZONE-R3-E1
RACK-R3-Z5E-R1-08 | 45 | LL-R3-E | 85% | 38.25 | CDU-R3-E | 6.75 | AIRZONE-R3-E1
RACK-R3-Z5E-R1-09 | 45 | LL-R3-E | 85% | 38.25 | CDU-R3-E | 6.75 | AIRZONE-R3-E1
RACK-R3-Z5E-R1-10 | 45 | LL-R3-E | 85% | 38.25 | CDU-R3-E | 6.75 | AIRZONE-R3-E1
RACK-R3-Z5E-R1-11 | 45 | LL-R3-E | 85% | 38.25 | CDU-R3-E | 6.75 | AIRZONE-R3-E1
RACK-R3-Z5E-R1-12 | 45 | LL-R3-E | 85% | 38.25 | CDU-R3-E | 6.75 | AIRZONE-R3-E1
RACK-R3-Z5E-R2-01 | 45 | LL-R3-E | 85% | 38.25 | CDU-R3-E | 6.75 | AIRZONE-R3-E1
RACK-R3-Z5E-R2-02 | 45 | LL-R3-E | 85% | 38.25 | CDU-R3-E | 6.75 | AIRZONE-R3-E1
RACK-R3-Z5E-R2-03 | 45 | LL-R3-E | 85% | 38.25 | CDU-R3-E | 6.75 | AIRZONE-R3-E1
RACK-R3-Z5E-R2-04 | 45 | LL-R3-E | 85% | 38.25 | CDU-R3-E | 6.75 | AIRZONE-R3-E1
RACK-R3-Z5E-R2-05 | 45 | LL-R3-E | 85% | 38.25 | CDU-R3-E | 6.75 | AIRZONE-R3-E1
RACK-R3-Z5E-R2-06 | 45 | LL-R3-E | 85% | 38.25 | CDU-R3-E | 6.75 | AIRZONE-R3-E1
RACK-R3-Z5E-R2-07 | 45 | LL-R3-E | 85% | 38.25 | CDU-R3-E | 6.75 | AIRZONE-R3-E1
RACK-R3-Z5E-R2-08 | 45 | LL-R3-E | 85% | 38.25 | CDU-R3-E | 6.75 | AIRZONE-R3-E1
RACK-R3-Z5E-R2-09 | 45 | LL-R3-E | 85% | 38.25 | CDU-R3-E | 6.75 | AIRZONE-R3-E1
RACK-R3-Z5E-R2-10 | 45 | LL-R3-E | 85% | 38.25 | CDU-R3-E | 6.75 | AIRZONE-R3-E1
RACK-R3-Z5E-R2-11 | 45 | LL-R3-E | 85% | 38.25 | CDU-R3-E | 6.75 | AIRZONE-R3-E1
RACK-R3-Z5E-R2-12 | 45 | LL-R3-E | 85% | 38.25 | CDU-R3-E | 6.75 | AIRZONE-R3-E1
RACK-R3-Z6E-R1-01 | 45 | LL-R3-E | 85% | 38.25 | CDU-R3-E | 6.75 | AIRZONE-R3-E2
RACK-R3-Z6E-R1-02 | 45 | LL-R3-E | 85% | 38.25 | CDU-R3-E | 6.75 | AIRZONE-R3-E2
RACK-R3-Z6E-R1-03 | 45 | LL-R3-E | 85% | 38.25 | CDU-R3-E | 6.75 | AIRZONE-R3-E2
RACK-R3-Z6E-R1-04 | 45 | LL-R3-E | 85% | 38.25 | CDU-R3-E | 6.75 | AIRZONE-R3-E2
RACK-R3-Z6E-R1-05 | 45 | LL-R3-E | 85% | 38.25 | CDU-R3-E | 6.75 | AIRZONE-R3-E2
RACK-R3-Z6E-R1-06 | 45 | LL-R3-E | 85% | 38.25 | CDU-R3-E | 6.75 | AIRZONE-R3-E2
RACK-R3-Z6E-R1-07 | 45 | LL-R3-E | 85% | 38.25 | CDU-R3-E | 6.75 | AIRZONE-R3-E2
RACK-R3-Z6E-R1-08 | 45 | LL-R3-E | 85% | 38.25 | CDU-R3-E | 6.75 | AIRZONE-R3-E2
RACK-R3-Z6E-R1-09 | 45 | LL-R3-E | 85% | 38.25 | CDU-R3-E | 6.75 | AIRZONE-R3-E2
RACK-R3-Z6E-R1-10 | 45 | LL-R3-E | 85% | 38.25 | CDU-R3-E | 6.75 | AIRZONE-R3-E2
RACK-R3-Z6E-R1-11 | 45 | LL-R3-E | 85% | 38.25 | CDU-R3-E | 6.75 | AIRZONE-R3-E2
RACK-R3-Z6E-R1-12 | 45 | LL-R3-E | 85% | 38.25 | CDU-R3-E | 6.75 | AIRZONE-R3-E2
RACK-R3-Z6E-R2-01 | 45 | LL-R3-E | 85% | 38.25 | CDU-R3-E | 6.75 | AIRZONE-R3-E2
RACK-R3-Z6E-R2-02 | 45 | LL-R3-E | 85% | 38.25 | CDU-R3-E | 6.75 | AIRZONE-R3-E2
RACK-R3-Z6E-R2-03 | 45 | LL-R3-E | 85% | 38.25 | CDU-R3-E | 6.75 | AIRZONE-R3-E2
RACK-R3-Z6E-R2-04 | 45 | LL-R3-E | 85% | 38.25 | CDU-R3-E | 6.75 | AIRZONE-R3-E2
RACK-R3-Z6E-R2-05 | 45 | LL-R3-E | 85% | 38.25 | CDU-R3-E | 6.75 | AIRZONE-R3-E2
RACK-R3-Z6E-R2-06 | 45 | LL-R3-E | 85% | 38.25 | CDU-R3-E | 6.75 | AIRZONE-R3-E2
RACK-R3-Z6E-R2-07 | 45 | LL-R3-E | 85% | 38.25 | CDU-R3-E | 6.75 | AIRZONE-R3-E2
RACK-R3-Z6E-R2-08 | 45 | LL-R3-E | 85% | 38.25 | CDU-R3-E | 6.75 | AIRZONE-R3-E2
RACK-R3-Z6E-R2-09 | 45 | LL-R3-E | 85% | 38.25 | CDU-R3-E | 6.75 | AIRZONE-R3-E2
RACK-R3-Z6E-R2-10 | 45 | LL-R3-E | 85% | 38.25 | CDU-R3-E | 6.75 | AIRZONE-R3-E2
RACK-R3-Z6E-R2-11 | 45 | LL-R3-E | 85% | 38.25 | CDU-R3-E | 6.75 | AIRZONE-R3-E2
RACK-R3-Z6E-R2-12 | 45 | LL-R3-E | 85% | 38.25 | CDU-R3-E | 6.75 | AIRZONE-R3-E2
RACK-R4-Z1-R1-01 | 20 | LL-R4 | 70% | 14 | CDU-R4 | 6 | AIRZONE-R4
RACK-R4-Z1-R1-02 | 20 | LL-R4 | 70% | 14 | CDU-R4 | 6 | AIRZONE-R4
RACK-R4-Z1-R1-03 | 20 | LL-R4 | 70% | 14 | CDU-R4 | 6 | AIRZONE-R4
RACK-R4-Z1-R1-04 | 20 | LL-R4 | 70% | 14 | CDU-R4 | 6 | AIRZONE-R4
RACK-R4-Z1-R1-05 | 20 | LL-R4 | 70% | 14 | CDU-R4 | 6 | AIRZONE-R4
RACK-R4-Z1-R1-06 | 20 | LL-R4 | 70% | 14 | CDU-R4 | 6 | AIRZONE-R4
RACK-R4-Z1-R1-07 | 20 | LL-R4 | 70% | 14 | CDU-R4 | 6 | AIRZONE-R4
RACK-R4-Z1-R1-08 | 20 | LL-R4 | 70% | 14 | CDU-R4 | 6 | AIRZONE-R4
RACK-R4-Z1-R1-09 | 20 | LL-R4 | 70% | 14 | CDU-R4 | 6 | AIRZONE-R4
RACK-R4-Z1-R1-10 | 20 | LL-R4 | 70% | 14 | CDU-R4 | 6 | AIRZONE-R4
RACK-R4-Z1-R1-11 | 20 | LL-R4 | 70% | 14 | CDU-R4 | 6 | AIRZONE-R4
RACK-R4-Z1-R1-12 | 20 | LL-R4 | 70% | 14 | CDU-R4 | 6 | AIRZONE-R4
RACK-R4-Z1-R2-01 | 20 | LL-R4 | 70% | 14 | CDU-R4 | 6 | AIRZONE-R4
RACK-R4-Z1-R2-02 | 20 | LL-R4 | 70% | 14 | CDU-R4 | 6 | AIRZONE-R4
RACK-R4-Z1-R2-03 | 20 | LL-R4 | 70% | 14 | CDU-R4 | 6 | AIRZONE-R4
RACK-R4-Z1-R2-04 | 20 | LL-R4 | 70% | 14 | CDU-R4 | 6 | AIRZONE-R4
RACK-R4-Z1-R2-05 | 20 | LL-R4 | 70% | 14 | CDU-R4 | 6 | AIRZONE-R4
RACK-R4-Z1-R2-06 | 20 | LL-R4 | 70% | 14 | CDU-R4 | 6 | AIRZONE-R4
RACK-R4-Z1-R2-07 | 20 | LL-R4 | 70% | 14 | CDU-R4 | 6 | AIRZONE-R4
RACK-R4-Z1-R2-08 | 20 | LL-R4 | 70% | 14 | CDU-R4 | 6 | AIRZONE-R4
RACK-R4-Z1-R2-09 | 20 | LL-R4 | 70% | 14 | CDU-R4 | 6 | AIRZONE-R4
RACK-R4-Z1-R2-10 | 20 | LL-R4 | 70% | 14 | CDU-R4 | 6 | AIRZONE-R4
RACK-R4-Z1-R2-11 | 20 | LL-R4 | 70% | 14 | CDU-R4 | 6 | AIRZONE-R4
RACK-R4-Z1-R2-12 | 20 | LL-R4 | 70% | 14 | CDU-R4 | 6 | AIRZONE-R4
RACK-R5-Z1W-R1-01 | 60 | LL-R5-W | 85% | 51 | CDU-R5-W | 9 | AIRZONE-R5-W
RACK-R5-Z1W-R1-02 | 60 | LL-R5-W | 85% | 51 | CDU-R5-W | 9 | AIRZONE-R5-W
RACK-R5-Z1W-R1-03 | 60 | LL-R5-W | 85% | 51 | CDU-R5-W | 9 | AIRZONE-R5-W
RACK-R5-Z1W-R1-04 | 60 | LL-R5-W | 85% | 51 | CDU-R5-W | 9 | AIRZONE-R5-W
RACK-R5-Z1W-R1-05 | 60 | LL-R5-W | 85% | 51 | CDU-R5-W | 9 | AIRZONE-R5-W
RACK-R5-Z1W-R1-06 | 60 | LL-R5-W | 85% | 51 | CDU-R5-W | 9 | AIRZONE-R5-W
RACK-R5-Z1W-R1-07 | 60 | LL-R5-W | 85% | 51 | CDU-R5-W | 9 | AIRZONE-R5-W
RACK-R5-Z1W-R1-08 | 60 | LL-R5-W | 85% | 51 | CDU-R5-W | 9 | AIRZONE-R5-W
RACK-R5-Z1W-R1-09 | 60 | LL-R5-W | 85% | 51 | CDU-R5-W | 9 | AIRZONE-R5-W
RACK-R5-Z1W-R1-10 | 60 | LL-R5-W | 85% | 51 | CDU-R5-W | 9 | AIRZONE-R5-W
RACK-R5-Z1W-R1-11 | 60 | LL-R5-W | 85% | 51 | CDU-R5-W | 9 | AIRZONE-R5-W
RACK-R5-Z1W-R1-12 | 60 | LL-R5-W | 85% | 51 | CDU-R5-W | 9 | AIRZONE-R5-W
RACK-R5-Z1W-R2-01 | 60 | LL-R5-W | 85% | 51 | CDU-R5-W | 9 | AIRZONE-R5-W
RACK-R5-Z1W-R2-02 | 60 | LL-R5-W | 85% | 51 | CDU-R5-W | 9 | AIRZONE-R5-W
RACK-R5-Z1W-R2-03 | 60 | LL-R5-W | 85% | 51 | CDU-R5-W | 9 | AIRZONE-R5-W
RACK-R5-Z1W-R2-04 | 60 | LL-R5-W | 85% | 51 | CDU-R5-W | 9 | AIRZONE-R5-W
RACK-R5-Z1W-R2-05 | 60 | LL-R5-W | 85% | 51 | CDU-R5-W | 9 | AIRZONE-R5-W
RACK-R5-Z1W-R2-06 | 60 | LL-R5-W | 85% | 51 | CDU-R5-W | 9 | AIRZONE-R5-W
RACK-R5-Z1W-R2-07 | 60 | LL-R5-W | 85% | 51 | CDU-R5-W | 9 | AIRZONE-R5-W
RACK-R5-Z1W-R2-08 | 60 | LL-R5-W | 85% | 51 | CDU-R5-W | 9 | AIRZONE-R5-W
RACK-R5-Z1W-R2-09 | 60 | LL-R5-W | 85% | 51 | CDU-R5-W | 9 | AIRZONE-R5-W
RACK-R5-Z1W-R2-10 | 60 | LL-R5-W | 85% | 51 | CDU-R5-W | 9 | AIRZONE-R5-W
RACK-R5-Z1W-R2-11 | 60 | LL-R5-W | 85% | 51 | CDU-R5-W | 9 | AIRZONE-R5-W
RACK-R5-Z1W-R2-12 | 60 | LL-R5-W | 85% | 51 | CDU-R5-W | 9 | AIRZONE-R5-W
RACK-R5-Z2E-R1-01 | 60 | LL-R5-E | 85% | 51 | CDU-R5-E | 9 | AIRZONE-R5-E
RACK-R5-Z2E-R1-02 | 60 | LL-R5-E | 85% | 51 | CDU-R5-E | 9 | AIRZONE-R5-E
RACK-R5-Z2E-R1-03 | 60 | LL-R5-E | 85% | 51 | CDU-R5-E | 9 | AIRZONE-R5-E
RACK-R5-Z2E-R1-04 | 60 | LL-R5-E | 85% | 51 | CDU-R5-E | 9 | AIRZONE-R5-E
RACK-R5-Z2E-R1-05 | 60 | LL-R5-E | 85% | 51 | CDU-R5-E | 9 | AIRZONE-R5-E
RACK-R5-Z2E-R1-06 | 60 | LL-R5-E | 85% | 51 | CDU-R5-E | 9 | AIRZONE-R5-E
RACK-R5-Z2E-R1-07 | 60 | LL-R5-E | 85% | 51 | CDU-R5-E | 9 | AIRZONE-R5-E
RACK-R5-Z2E-R1-08 | 60 | LL-R5-E | 85% | 51 | CDU-R5-E | 9 | AIRZONE-R5-E
RACK-R5-Z2E-R1-09 | 60 | LL-R5-E | 85% | 51 | CDU-R5-E | 9 | AIRZONE-R5-E
RACK-R5-Z2E-R1-10 | 60 | LL-R5-E | 85% | 51 | CDU-R5-E | 9 | AIRZONE-R5-E
RACK-R5-Z2E-R1-11 | 60 | LL-R5-E | 85% | 51 | CDU-R5-E | 9 | AIRZONE-R5-E
RACK-R5-Z2E-R1-12 | 60 | LL-R5-E | 85% | 51 | CDU-R5-E | 9 | AIRZONE-R5-E
RACK-R5-Z2E-R2-01 | 60 | LL-R5-E | 85% | 51 | CDU-R5-E | 9 | AIRZONE-R5-E
RACK-R5-Z2E-R2-02 | 60 | LL-R5-E | 85% | 51 | CDU-R5-E | 9 | AIRZONE-R5-E
RACK-R5-Z2E-R2-03 | 60 | LL-R5-E | 85% | 51 | CDU-R5-E | 9 | AIRZONE-R5-E
RACK-R5-Z2E-R2-04 | 60 | LL-R5-E | 85% | 51 | CDU-R5-E | 9 | AIRZONE-R5-E
RACK-R5-Z2E-R2-05 | 60 | LL-R5-E | 85% | 51 | CDU-R5-E | 9 | AIRZONE-R5-E
RACK-R5-Z2E-R2-06 | 60 | LL-R5-E | 85% | 51 | CDU-R5-E | 9 | AIRZONE-R5-E
RACK-R5-Z2E-R2-07 | 60 | LL-R5-E | 85% | 51 | CDU-R5-E | 9 | AIRZONE-R5-E
RACK-R5-Z2E-R2-08 | 60 | LL-R5-E | 85% | 51 | CDU-R5-E | 9 | AIRZONE-R5-E
RACK-R5-Z2E-R2-09 | 60 | LL-R5-E | 85% | 51 | CDU-R5-E | 9 | AIRZONE-R5-E
RACK-R5-Z2E-R2-10 | 60 | LL-R5-E | 85% | 51 | CDU-R5-E | 9 | AIRZONE-R5-E
RACK-R5-Z2E-R2-11 | 60 | LL-R5-E | 85% | 51 | CDU-R5-E | 9 | AIRZONE-R5-E
RACK-R5-Z2E-R2-12 | 60 | LL-R5-E | 85% | 51 | CDU-R5-E | 9 | AIRZONE-R5-E
RACK-R1-Z1-R1-01 | 15 | LL-R1 | 50% | 7.5 | CDU-R1 | 7.5 | AIRZONE-R1
RACK-R1-Z1-R1-02 | 15 | LL-R1 | 50% | 7.5 | CDU-R1 | 7.5 | AIRZONE-R1
RACK-R1-Z1-R1-03 | 15 | LL-R1 | 50% | 7.5 | CDU-R1 | 7.5 | AIRZONE-R1
RACK-R1-Z1-R1-04 | 15 | LL-R1 | 50% | 7.5 | CDU-R1 | 7.5 | AIRZONE-R1
RACK-R1-Z1-R1-05 | 15 | LL-R1 | 50% | 7.5 | CDU-R1 | 7.5 | AIRZONE-R1
RACK-R1-Z1-R1-06 | 15 | LL-R1 | 50% | 7.5 | CDU-R1 | 7.5 | AIRZONE-R1
RACK-R1-Z1-R2-01 | 15 | LL-R1 | 50% | 7.5 | CDU-R1 | 7.5 | AIRZONE-R1
RACK-R1-Z1-R2-02 | 15 | LL-R1 | 50% | 7.5 | CDU-R1 | 7.5 | AIRZONE-R1
RACK-R1-Z1-R2-03 | 15 | LL-R1 | 50% | 7.5 | CDU-R1 | 7.5 | AIRZONE-R1
RACK-R1-Z1-R2-04 | 15 | LL-R1 | 50% | 7.5 | CDU-R1 | 7.5 | AIRZONE-R1
RACK-R1-Z1-R2-05 | 15 | LL-R1 | 50% | 7.5 | CDU-R1 | 7.5 | AIRZONE-R1
RACK-R1-Z1-R2-06 | 15 | LL-R1 | 50% | 7.5 | CDU-R1 | 7.5 | AIRZONE-R1
RACK-R1-Z2-R1-01 | 15 | LL-R1 | 50% | 7.5 | CDU-R1 | 7.5 | AIRZONE-R1
RACK-R1-Z2-R1-02 | 15 | LL-R1 | 50% | 7.5 | CDU-R1 | 7.5 | AIRZONE-R1
RACK-R1-Z2-R1-03 | 15 | LL-R1 | 50% | 7.5 | CDU-R1 | 7.5 | AIRZONE-R1
RACK-R1-Z2-R1-04 | 15 | LL-R1 | 50% | 7.5 | CDU-R1 | 7.5 | AIRZONE-R1
RACK-R1-Z2-R1-05 | 15 | LL-R1 | 50% | 7.5 | CDU-R1 | 7.5 | AIRZONE-R1
RACK-R1-Z2-R1-06 | 15 | LL-R1 | 50% | 7.5 | CDU-R1 | 7.5 | AIRZONE-R1
RACK-R1-Z2-R2-01 | 15 | LL-R1 | 50% | 7.5 | CDU-R1 | 7.5 | AIRZONE-R1
RACK-R1-Z2-R2-02 | 15 | LL-R1 | 50% | 7.5 | CDU-R1 | 7.5 | AIRZONE-R1
RACK-R1-Z2-R2-03 | 15 | LL-R1 | 50% | 7.5 | CDU-R1 | 7.5 | AIRZONE-R1
RACK-R1-Z2-R2-04 | 15 | LL-R1 | 50% | 7.5 | CDU-R1 | 7.5 | AIRZONE-R1
RACK-R1-Z2-R2-05 | 15 | LL-R1 | 50% | 7.5 | CDU-R1 | 7.5 | AIRZONE-R1
RACK-R1-Z2-R2-06 | 15 | LL-R1 | 50% | 7.5 | CDU-R1 | 7.5 | AIRZONE-R1
RACK-R2-Z1-R1-01 | 15 | LL-R2 | 50% | 7.5 | CDU-R2 | 7.5 | AIRZONE-R2
RACK-R2-Z1-R1-02 | 15 | LL-R2 | 50% | 7.5 | CDU-R2 | 7.5 | AIRZONE-R2
RACK-R2-Z1-R1-03 | 15 | LL-R2 | 50% | 7.5 | CDU-R2 | 7.5 | AIRZONE-R2
RACK-R2-Z1-R1-04 | 15 | LL-R2 | 50% | 7.5 | CDU-R2 | 7.5 | AIRZONE-R2
RACK-R2-Z1-R1-05 | 15 | LL-R2 | 50% | 7.5 | CDU-R2 | 7.5 | AIRZONE-R2
RACK-R2-Z1-R1-06 | 15 | LL-R2 | 50% | 7.5 | CDU-R2 | 7.5 | AIRZONE-R2
RACK-R2-Z1-R2-01 | 15 | LL-R2 | 50% | 7.5 | CDU-R2 | 7.5 | AIRZONE-R2
RACK-R2-Z1-R2-02 | 15 | LL-R2 | 50% | 7.5 | CDU-R2 | 7.5 | AIRZONE-R2
RACK-R2-Z1-R2-03 | 15 | LL-R2 | 50% | 7.5 | CDU-R2 | 7.5 | AIRZONE-R2
RACK-R2-Z1-R2-04 | 15 | LL-R2 | 50% | 7.5 | CDU-R2 | 7.5 | AIRZONE-R2
RACK-R2-Z1-R2-05 | 15 | LL-R2 | 50% | 7.5 | CDU-R2 | 7.5 | AIRZONE-R2
RACK-R2-Z1-R2-06 | 15 | LL-R2 | 50% | 7.5 | CDU-R2 | 7.5 | AIRZONE-R2
RACK-R2-Z2-R1-01 | 15 | LL-R2 | 50% | 7.5 | CDU-R2 | 7.5 | AIRZONE-R2
RACK-R2-Z2-R1-02 | 15 | LL-R2 | 50% | 7.5 | CDU-R2 | 7.5 | AIRZONE-R2
RACK-R2-Z2-R1-03 | 15 | LL-R2 | 50% | 7.5 | CDU-R2 | 7.5 | AIRZONE-R2
RACK-R2-Z2-R1-04 | 15 | LL-R2 | 50% | 7.5 | CDU-R2 | 7.5 | AIRZONE-R2
RACK-R2-Z2-R1-05 | 15 | LL-R2 | 50% | 7.5 | CDU-R2 | 7.5 | AIRZONE-R2
RACK-R2-Z2-R1-06 | 15 | LL-R2 | 50% | 7.5 | CDU-R2 | 7.5 | AIRZONE-R2
RACK-R2-Z2-R2-01 | 15 | LL-R2 | 50% | 7.5 | CDU-R2 | 7.5 | AIRZONE-R2
RACK-R2-Z2-R2-02 | 15 | LL-R2 | 50% | 7.5 | CDU-R2 | 7.5 | AIRZONE-R2
RACK-R2-Z2-R2-03 | 15 | LL-R2 | 50% | 7.5 | CDU-R2 | 7.5 | AIRZONE-R2
RACK-R2-Z2-R2-04 | 15 | LL-R2 | 50% | 7.5 | CDU-R2 | 7.5 | AIRZONE-R2
RACK-R2-Z2-R2-05 | 15 | LL-R2 | 50% | 7.5 | CDU-R2 | 7.5 | AIRZONE-R2
RACK-R2-Z2-R2-06 | 15 | LL-R2 | 50% | 7.5 | CDU-R2 | 7.5 | AIRZONE-R2

## Cooling-Dist
Cooling Distribution | CRAH | Acitve | CRAH Rating (kW) | Air Zone | Design DeltaT_Rack | Max inlet air temp | Inlet temp operational setpoint | Cold aisle supply temp | CDU | Liquid Loop | Liquid Loop Capacity (kW) | Design DetlaT_Device (Celcius) | Max CDU branch inlet temp (Celcius) | CDU branch inlet temp operational setpoint | Supply Temp_Device (Celcius)
CDIST-01 | ACU-01-A | TRUE | 150 | AIRZONE-R1 | 12 | 28 | 27 | 24
CDIST-01 | ACU-01-B | TRUE | 150 | AIRZONE-R1 | 12 | 28 | 27 | 24
CDIST-01 | ACU-02-A | TRUE | 150 | AIRZONE-R2 | 12 | 28 | 27 | 24
CDIST-01 | ACU-02-B | TRUE | 150 | AIRZONE-R2 | 12 | 28 | 27 | 24
CDIST-A-02 | CRAH-AZ-R3-E1-01 | TRUE | 100 | AIRZONE-R3-E1 | 12 | 28 | 27 | 24
CDIST-A-02 | CRAH-AZ-R3-E1-02 | TRUE | 100 | AIRZONE-R3-E1 | 12 | 28 | 27 | 24
CDIST-A-02 | CRAH-AZ-R3-E1-03 | TRUE | 100 | AIRZONE-R3-E1 | 12 | 28 | 27 | 24
CDIST-A-02 | CRAH-AZ-R3-E1-04 | TRUE | 100 | AIRZONE-R3-E1 | 12 | 28 | 27 | 24
CDIST-A-02 | CRAH-AZ-R3-E1-05 | FALSE | 100 | AIRZONE-R3-E1 | 12 | 28 | 27 | 24
CDIST-A-02 | CRAH-AZ-R3-E2-01 | TRUE | 100 | AIRZONE-R3-E2 | 12 | 28 | 27 | 24
CDIST-A-02 | CRAH-AZ-R3-E2-02 | TRUE | 100 | AIRZONE-R3-E2 | 12 | 28 | 27 | 24
CDIST-A-02 | CRAH-AZ-R3-E2-03 | FALSE | 100 | AIRZONE-R3-E2 | 12 | 28 | 27 | 24
CDIST-A-02 | CRAH-AZ-R3-W1-01 | TRUE | 100 | AIRZONE-R3-W1 | 12 | 28 | 27 | 24
CDIST-A-02 | CRAH-AZ-R3-W1-02 | TRUE | 100 | AIRZONE-R3-W1 | 12 | 28 | 27 | 24
CDIST-A-02 | CRAH-AZ-R3-W1-03 | TRUE | 100 | AIRZONE-R3-W1 | 12 | 28 | 27 | 24
CDIST-A-02 | CRAH-AZ-R3-W1-04 | TRUE | 100 | AIRZONE-R3-W1 | 12 | 28 | 27 | 24
CDIST-A-02 | CRAH-AZ-R3-W1-05 | FALSE | 100 | AIRZONE-R3-W1 | 12 | 28 | 27 | 24
CDIST-A-02 | CRAH-AZ-R3-W2-01 | TRUE | 100 | AIRZONE-R3-W2 | 12 | 28 | 27 | 24
CDIST-A-02 | CRAH-AZ-R3-W2-02 | TRUE | 100 | AIRZONE-R3-W2 | 12 | 28 | 27 | 24
CDIST-A-02 | CRAH-AZ-R3-W2-03 | FALSE | 100 | AIRZONE-R3-W2 | 12 | 28 | 27 | 24
CDIST-A-02 | CRAH-AZ-R4-01 | TRUE | 100 | AIRZONE-R4 | 12 | 28 | 27 | 24
CDIST-A-02 | CRAH-AZ-R4-02 | TRUE | 100 | AIRZONE-R4 | 12 | 28 | 27 | 24
CDIST-A-02 | CRAH-AZ-R4-03 | FALSE | 100 | AIRZONE-R4 | 12 | 28 | 27 | 24
CDIST-A-02 | CRAH-AZ-R5-W-01 | TRUE | 100 | AIRZONE-R5-W | 12 | 28 | 27 | 24
CDIST-A-02 | CRAH-AZ-R5-W-02 | TRUE | 100 | AIRZONE-R5-W | 12 | 28 | 27 | 24
CDIST-A-02 | CRAH-AZ-R5-W-03 | TRUE | 100 | AIRZONE-R5-W | 12 | 28 | 27 | 24
CDIST-A-02 | CRAH-AZ-R5-W-04 | FALSE | 100 | AIRZONE-R5-W | 12 | 28 | 27 | 24
CDIST-A-02 | CRAH-AZ-R5-E-05 | TRUE | 100 | AIRZONE-R5-E | 12 | 28 | 27 | 24
CDIST-A-02 | CRAH-AZ-R5-E-06 | TRUE | 100 | AIRZONE-R5-E | 12 | 28 | 27 | 24
CDIST-A-02 | CRAH-AZ-R5-E-07 | TRUE | 100 | AIRZONE-R5-E | 12 | 28 | 27 | 24
CDIST-A-02 | CRAH-AZ-R5-E-08 | FALSE | 100 | AIRZONE-R5-E | 12 | 28 | 27 | 24
CDIST-01 | [8 empty] | CDU-R1 | LL-R1 | 200
CDIST-01 | [8 empty] | CDU-R2 | LL-R2 | 200
CDIST-L-02 | [8 empty] | CDU-R3-E | LL-R3-E | 2000 | 7 | 32 | 29 | 22
CDIST-L-02 | [8 empty] | CDU-R3-W | LL-R3-W | 1000 | 7 | 32 | 29 | 22
CDIST-L-02 | [8 empty] | CDU-R4 | LL-R4 | 500 | 7 | 32 | 29 | 22
CDIST-L-02 | [8 empty] | CDU-R5-W | LL-R5-W | 1500
CDIST-L-02 | [8 empty] | CDU-R5-E | LL-R5-E | 1500
CDU-R1
CDU-R2
Note on O1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Design parameters
Note on P1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Design parameters

## Constraints
Constraint Type | Node Type | Constraint Node | Rack_Circuit_Capacity_(design) | Operational Capacity Name | Operational Capacity | Device Capacity Name | Device Capacity (design) | Device Rating Name | Device Rating | Capacity Cell | CC AZ Capacity | CC LL Capacity | CC RPP(A) Capacity | CC RPP(B) Capacity | SJ-Meridian-C01-PP01 LOAD | SJ-Pacific-C01-PD01 LOAD | SJ-Pacific-C01-PD02 LOAD | SJ-Pacific-C01-PD03 LOAD | SJ-Pacific-C01-PD04 LOAD | SJ-Keystone-C01-PP01 LOAD | TOTAL LOAD ALL PP | TOTAL LOAD with SJ-PACIFIC-C01-PD01 | TOTAL LOAD with SJ-PACIFIC-C01-PD02 | TOTAL LOAD with SJ-PACIFIC-C01-PD03 | TOTAL LOAD with SJ-PACIFIC-C01-PD04 | SJ-Meridian-C01-PP01 COUNT | SJ-Pacific-C01-PD01 COUNT | SJ-Pacific-C01-PD02 COUNT | SJ-Pacific-C01-PD03 COUNT | SJ-Pacific-C01-PD04 COUNT | SJ-Keystone-C01-PP01 COUNT | TOTAL COUNT ALL PP | TOTAL COUNT with SJ-PACIFIC-C01-PD01 | TOTAL COUNT with SJ-PACIFIC-C01-PD02 | TOTAL COUNT with SJ-PACIFIC-C01-PD03 | TOTAL COUNT with SJ-PACIFIC-C01-PD04 | Rack_Inlet_Setpoint | Loop_Supply_Setpoint | Loop_DeltaT_(design) (celcius) | CDU.Pump_Capacity (L/s) | Rack_DeltaT_(design) (celsius) | AirZone.Maximum_Air_Flow (m3/s) | ColdAisle_Supply_Temp | LL.Maximum_Flow_Rate | RPP_BreakerPole_Capacity | AirCoolUnit.Maximum_Air_Flow (m3/s) | Rack_Count | CC Thermal Capacity | CC Power Capacity
Row | Row | ROW-R1-Z1-R1 | 90 | [6 empty] | CC-R1R2 |  |  |  |  | 90 | 0 | 0 | 0 | 0 | 0 | 90 | 90 | 90 | 90 | 90 | 6 | 0 | 0 | 0 | 0 | 0 | 6 | 6 | 6 | 6 | 6 |  | Loop_DeltaT_(design)
Row | Row | ROW-R1-Z1-R2 | 90 | [6 empty] | CC-R1R2 |  |  |  |  | 60 | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 60 | 60 | 60 | 6 | 0 | 0 | 0 | 0 | 0 | 6 | 6 | 6 | 6 | 6
Row | Row | ROW-R1-Z2-R1 | 90 | [6 empty] | CC-R1R2 |  |  |  |  | 90 | 0 | 0 | 0 | 0 | 0 | 90 | 90 | 90 | 90 | 90 | 6 | 0 | 0 | 0 | 0 | 0 | 6 | 6 | 6 | 6 | 6
Row | Row | ROW-R1-Z2-R2 | 90 | [6 empty] | CC-R1R2 |  |  |  |  | 60 | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 60 | 60 | 60 | 6 | 0 | 0 | 0 | 0 | 0 | 6 | 6 | 6 | 6 | 6
Row | Row | ROW-R2-Z1-R1 | 90 | [6 empty] | CC-R1R2 |  |  |  |  | 90 | 0 | 0 | 0 | 0 | 0 | 90 | 90 | 90 | 90 | 90 | 6 | 0 | 0 | 0 | 0 | 0 | 6 | 6 | 6 | 6 | 6
Row | Row | ROW-R2-Z1-R2 | 90 | [6 empty] | CC-R1R2 |  |  |  |  | 60 | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 60 | 60 | 60 | 6 | 0 | 0 | 0 | 0 | 0 | 6 | 6 | 6 | 6 | 6
Row | Row | ROW-R2-Z2-R1 | 90 | [6 empty] | CC-R1R2 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Row | Row | ROW-R2-Z2-R2 | 90 | [6 empty] | CC-R1R2 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Row | Row | ROW-R3-Z1W-R1 | 360 | [6 empty] | CC-R3 |  |  |  |  | 0 | 360 | 240 | 0 | 0 | 0 | 0 | 360 | 240 | 0 | 0 | 0 | 12 | 8 | 0 | 0 | 0 | 0 | 12 | 8 | 0 | 0
Row | Row | ROW-R3-Z1W-R2 | 360 | [6 empty] | CC-R3 |  |  |  |  | 0 | 120 | 300 | 0 | 0 | 0 | 0 | 120 | 300 | 0 | 0 | 0 | 4 | 10 | 0 | 0 | 0 | 0 | 4 | 10 | 0 | 0
Row | Row | ROW-R3-Z2W-R1 | 360 | [6 empty] | CC-R3 |  |  |  |  | 0 | 360 | 240 | 0 | 0 | 0 | 0 | 360 | 240 | 0 | 0 | 0 | 12 | 8 | 0 | 0 | 0 | 0 | 12 | 8 | 0 | 0
Row | Row | ROW-R3-Z2W-R2 | 360 | [6 empty] | CC-R3 |  |  |  |  | 0 | 360 | 120 | 0 | 0 | 0 | 0 | 360 | 120 | 0 | 0 | 0 | 12 | 4 | 0 | 0 | 0 | 0 | 12 | 4 | 0 | 0
Row | Row | ROW-R3-Z3W-R1 | 360 | [6 empty] | CC-R3 |  |  |  |  | 0 | 360 | 360 | 0 | 0 | 0 | 0 | 360 | 360 | 0 | 0 | 0 | 12 | 12 | 0 | 0 | 0 | 0 | 12 | 12 | 0 | 0
Row | Row | ROW-R3-Z3W-R2 | 360 | [6 empty] | CC-R3 |  |  |  |  | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0
Row | Row | ROW-R3-Z4E-R1 | 540 | [6 empty] | CC-R3 |  |  |  |  | 0 | 0 | 0 | 240 | 360 | 0 | 0 | 0 | 0 | 240 | 360 | 0 | 0 | 0 | 8 | 12 | 0 | 0 | 0 | 0 | 8 | 12
Row | Row | ROW-R3-Z4E-R2 | 540 | [6 empty] | CC-R3 |  |  |  |  | 0 | 0 | 0 | 240 | 360 | 0 | 0 | 0 | 0 | 240 | 360 | 0 | 0 | 0 | 8 | 12 | 0 | 0 | 0 | 0 | 8 | 12
Row | Row | ROW-R3-Z5E-R1 | 540 | [6 empty] | CC-R3 |  |  |  |  | 0 | 0 | 0 | 360 | 360 | 0 | 0 | 0 | 0 | 360 | 360 | 0 | 0 | 0 | 12 | 12 | 0 | 0 | 0 | 0 | 12 | 12
Row | Row | ROW-R3-Z5E-R2 | 540 | [6 empty] | CC-R3 |  |  |  |  | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 12 | 0
Row | Row | ROW-R3-Z6E-R1 | 540 | [6 empty] | CC-R3 |  |  |  |  | 0 | 0 | 0 | 360 | 360 | 0 | 0 | 0 | 0 | 360 | 360 | 0 | 0 | 0 | 12 | 12 | 0 | 0 | 0 | 0 | 12 | 12
Row | Row | ROW-R3-Z6E-R2 | 540 | [6 empty] | CC-R3 |  |  |  |  | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 4
Row | Row | ROW-R4-Z1-R1 | 240 | [6 empty] | CC-R4 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Row | Row | ROW-R4-Z1-R2 | 240 | [6 empty] | CC-R4 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Row | Row | ROW-R5-Z1W-R1 | 720 | [6 empty] | CC-R5W |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Row | Row | ROW-R5-Z1W-R2 | 720 | [6 empty] | CC-R5W |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Row | Row | ROW-R5-Z2E-R1 | 720 | [6 empty] | CC-R5E |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 720 | 720 | 720 | 720 | 720 | 720 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 12 | 12 | 12 | 12
Row | Row | ROW-R5-Z2E-R2 | 720 | [6 empty] | CC-R5E |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 675 | 675 | 675 | 675 | 675 | 675 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 12 | 12 | 12 | 12
RPP(A) | RPP | RPP-R1-1 | 180 | RPP_Panel_Capacity_(design) | 230 |  |  | RPP_Panel_Capacity_(rated) | 288 | CC-R1R2 |  |  |  |  | 120 | 0 | 0 | 0 | 0 | 0 | 120 | 120 | 120 | 120 | 120 | 9 | 0 | 0 | 0 | 0 | 0 | 9 | 9 | 9 | 9 | 9 | [8 empty] | 54 |  | 12
RPP(A) | RPP | RPP-R1-2 | 180 | RPP_Panel_Capacity_(design) | 230 |  |  | RPP_Panel_Capacity_(rated) | 288 | CC-R1R2 |  |  |  |  | 120 | 0 | 0 | 0 | 0 | 0 | 120 | 120 | 120 | 120 | 120 | 9 | 0 | 0 | 0 | 0 | 0 | 9 | 9 | 9 | 9 | 9 | [8 empty] | 54 |  | 12
RPP(A) | RPP | RPP-R2-1 | 180 | RPP_Panel_Capacity_(design) | 230 |  |  | RPP_Panel_Capacity_(rated) | 288 | CC-R1R2 |  |  |  |  | 105 | 0 | 0 | 0 | 0 | 0 | 105 | 105 | 105 | 105 | 105 | 9 | 0 | 0 | 0 | 0 | 0 | 9 | 9 | 9 | 9 | 9 | [8 empty] | 54 |  | 12
RPP(A) | RPP | RPP-R2-2 | 180 | RPP_Panel_Capacity_(design) | 230 |  |  | RPP_Panel_Capacity_(rated) | 288 | CC-R1R2 |  |  |  |  | 105 | 0 | 0 | 0 | 0 | 0 | 105 | 105 | 105 | 105 | 105 | 9 | 0 | 0 | 0 | 0 | 0 | 9 | 9 | 9 | 9 | 9 | [8 empty] | 54 |  | 12
RPP(A) | RPP | RPP-R3-A1 | 1260 | RPP_Panel_Capacity_(design) | 920 |  |  | RPP_Panel_Capacity_(rated) | 1150 | CC-R3 |  |  |  |  | 0 | 960 | 660 | 0 | 120 | 0 | 0 | 960 | 660 | 0 | 120 | 0 | 32 | 22 | 0 | 4 | 0 | 0 | 32 | 22 | 0 | 4 | [8 empty] | 120 |  | 40
RPP(A) | RPP | RPP-R3-A2 | 1260 | RPP_Panel_Capacity_(design) | 920 |  |  | RPP_Panel_Capacity_(rated) | 1150 | CC-R3 |  |  |  |  | 0 | 600 | 900 | 0 | 120 | 0 | 0 | 600 | 900 | 0 | 120 | 0 | 20 | 30 | 0 | 4 | 0 | 0 | 20 | 30 | 0 | 4 | [8 empty] | 120 |  | 40
RPP(A) | RPP | RPP-R3-A3 | 1440 | RPP_Panel_Capacity_(design) | 920 |  |  | RPP_Panel_Capacity_(rated) | 1150 | CC-R3 |  |  |  |  | 0 | 0 | 0 | 780 | 660 | 0 | 0 | 0 | 0 | 780 | 660 | 0 | 0 | 0 | 26 | 22 | 0 | 0 | 0 | 0 | 26 | 22 | [8 empty] | 120 |  | 32
RPP(A) | RPP | RPP-R3-A4 | 1440 | RPP_Panel_Capacity_(design) | 920 |  |  | RPP_Panel_Capacity_(rated) | 1150 | CC-R3 |  |  |  |  | 0 | 0 | 0 | 780 | 660 | 0 | 0 | 0 | 0 | 780 | 660 | 0 | 0 | 0 | 26 | 22 | 0 | 0 | 0 | 0 | 26 | 22 | [8 empty] | 120 |  | 32
RPP(A) | RPP | RPP-R4-A5 | 240 | RPP_Panel_Capacity_(design) | 345 |  |  | RPP_Panel_Capacity_(rated) | 431 | CC-R4 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 84 |  | 12
RPP(A) | RPP | RPP-R4-A6 | 240 | RPP_Panel_Capacity_(design) | 345 |  |  | RPP_Panel_Capacity_(rated) | 431 | CC-R4 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 84 |  | 12
RPP(A) | RPP | RPP-R5-A1 | 720 | RPP_Panel_Capacity_(design) | 920 |  |  | RPP_Panel_Capacity_(rated) | 1150 | CC-R5W |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 84 |  | 12
RPP(A) | RPP | RPP-R5-A2 | 720 | RPP_Panel_Capacity_(design) | 920 |  |  | RPP_Panel_Capacity_(rated) | 1150 | CC-R5W |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 84 |  | 12
RPP(A) | RPP | RPP-R5-A3 | 720 | RPP_Panel_Capacity_(design) | 920 |  |  | RPP_Panel_Capacity_(rated) | 1150 | CC-R5E |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 720 | 720 | 720 | 720 | 720 | 720 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 12 | 12 | 12 | 12 | [8 empty] | 84 |  | 12
RPP(A) | RPP | RPP-R5-A4 | 720 | RPP_Panel_Capacity_(design) | 920 |  |  | RPP_Panel_Capacity_(rated) | 1150 | CC-R5E |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 675 | 675 | 675 | 675 | 675 | 675 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 12 | 12 | 12 | 12 | [8 empty] | 84 |  | 12
RPP(B) | RPP | RPP-R3-B1 | 1350 | RPP_Panel_Capacity_(design) | 1380 |  |  | RPP_Panel_Capacity_(rated) | 1725 | CC-R3 |  |  |  |  | 0 | 360 | 360 | 420 | 540 | 0 | 0 | 360 | 360 | 420 | 540 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 120 |  | 36
RPP(B) | RPP | RPP-R3-B2 | 1350 | RPP_Panel_Capacity_(design) | 1380 |  |  | RPP_Panel_Capacity_(rated) | 1725 | CC-R3 |  |  |  |  | 0 | 420 | 360 | 240 | 300 | 0 | 0 | 420 | 360 | 240 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 120 |  | 36
RPP(B) | RPP | RPP-R3-B3 | 1080 | RPP_Panel_Capacity_(design) | 920 |  |  | RPP_Panel_Capacity_(rated) | 1150 | CC-R3 |  |  |  |  | 0 | 780 | 840 | 0 | 0 | 0 | 0 | 780 | 840 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 120 |  | 36
RPP(B) | RPP | RPP-R3-B4 | 1620 | RPP_Panel_Capacity_(design) | 1380 |  |  | RPP_Panel_Capacity_(rated) | 1725 | CC-R3 |  |  |  |  | 0 | 0 | 0 | 900 | 720 | 0 | 0 | 0 | 0 | 900 | 720 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 120 |  | 36
RPP(B) | RPP | RPP-R4-B5 | 240 | RPP_Panel_Capacity_(design) | 345 |  |  | RPP_Panel_Capacity_(rated) | 431 | CC-R4 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 84 |  | 12
RPP(B) | RPP | RPP-R4-B6 | 240 | RPP_Panel_Capacity_(design) | 345 |  |  | RPP_Panel_Capacity_(rated) | 431 | CC-R4 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 84 |  | 12
RPP(B) | RPP | RPP-R5-B1 | 720 | RPP_Panel_Capacity_(design) | 920 |  |  | RPP_Panel_Capacity_(rated) | 1150 | CC-R5W |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 84 |  | 12
RPP(B) | RPP | RPP-R5-B2 | 720 | RPP_Panel_Capacity_(design) | 920 |  |  | RPP_Panel_Capacity_(rated) | 1150 | CC-R5W |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 84 |  | 12
RPP(B) | RPP | RPP-R5-B3 | 720 | RPP_Panel_Capacity_(design) | 920 |  |  | RPP_Panel_Capacity_(rated) | 1150 | CC-R5E |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 720 | 720 | 720 | 720 | 720 | 720 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 84 |  | 12
RPP(B) | RPP | RPP-R5-B4 | 720 | RPP_Panel_Capacity_(design) | 920 |  |  | RPP_Panel_Capacity_(rated) | 1150 | CC-R5E |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 675 | 675 | 675 | 675 | 675 | 675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 84 |  | 12
Liquid Loop | Liquid Loop | LL-R1 | 180 | LL_Cooling_Capacity | 200 |  |  |  |  | CC-R1R2 |  |  |  |  | 150 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 150 | 150 | 150 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 24 | 24 | 24 | 24 |  | 22 | 10 |  |  |  |  | 5
Liquid Loop | Liquid Loop | LL-R2 | 180 | LL_Cooling_Capacity | 200 |  |  |  |  | CC-R1R2 |  |  |  |  | 75 | 0 | 0 | 0 | 0 | 0 | 75 | 75 | 75 | 75 | 75 | 12 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 12 | 12 | 12 |  | 22 | 10 |  |  |  |  | 5
Liquid Loop | Liquid Loop | LL-R3-E | 2754 | LL_Cooling_Capacity | 2000 |  |  |  |  | CC-R3 |  |  |  |  | 0 | 0 | 0 | 1326 | 1326 | 0 | 0 | 0 | 0 | 1326 | 1326 | 0 | 0 | 0 | 52 | 52 | 0 | 0 | 0 | 0 | 52 | 52 |  | 22 | 10 |  |  |  |  | 48
Liquid Loop | Liquid Loop | LL-R3-W | 1620 | LL_Cooling_Capacity | 1000 |  |  |  |  | CC-R3 |  |  |  |  | 0 | 1170 | 1170 | 0 | 0 | 0 | 0 | 1170 | 1170 | 0 | 0 | 0 | 52 | 52 | 0 | 0 | 0 | 0 | 52 | 52 | 0 | 0 |  | 22 | 10 |  |  |  |  | 24
Liquid Loop | Liquid Loop | LL-R4 | 336 | LL_Cooling_Capacity | 500 |  |  |  |  | CC-R4 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 10 |  |  |  |  | 12
Liquid Loop | Liquid Loop | LL-R5-E | 1224 | LL_Cooling_Capacity | 1500 |  |  |  |  | CC-R5E |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 1185.75 | 1185.75 | 1185.75 | 1185.75 | 1185.75 | 1185.75 | 0 | 0 | 0 | 0 | 0 | 24 | 24 | 24 | 24 | 24 | 24 |  | 22 | 10 |  |  |  |  | 36
Liquid Loop | Liquid Loop | LL-R5-W | 1224 | LL_Cooling_Capacity | 1500 |  |  |  |  | CC-R5W |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 10 |  |  |  |  | 36
Air Zone | Air Zone | AIRZONE-R1 | 180 | AirZone_Cooling_Capacity | 270 |  |  |  |  | CC-R1R2 |  |  |  |  | 150 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 150 | 150 | 150 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 24 | 24 | 24 | 24 | 27 |  |  |  | 12 | 18.75 | 24
Air Zone | Air Zone | AIRZONE-R2 | 180 | AirZone_Cooling_Capacity | 270 |  |  |  |  | CC-R1R2 |  |  |  |  | 75 | 0 | 0 | 0 | 0 | 0 | 75 | 75 | 75 | 75 | 75 | 12 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 12 | 12 | 12 | 27 |  |  |  | 12 | 18.75 | 24
Air Zone | Air Zone | AIRZONE-R3-E1 | 324 | AirZone_Cooling_Capacity | 240 |  |  |  |  | CC-R3 |  |  |  |  | 0 | 0 | 0 | 180 | 162 | 0 | 0 | 0 | 0 | 180 | 162 | 0 | 0 | 0 | 40 | 36 | 0 | 0 | 0 | 0 | 40 | 36 | 27 |  |  |  | 12 | 16.6667 | 24
Air Zone | Air Zone | AIRZONE-R3-E2 | 162 | AirZone_Cooling_Capacity | 180 |  |  |  |  | CC-R3 |  |  |  |  | 0 | 0 | 0 | 54 | 72 | 0 | 0 | 0 | 0 | 54 | 72 | 0 | 0 | 0 | 12 | 16 | 0 | 0 | 0 | 0 | 12 | 16 | 27 |  |  |  | 12 | 12.5 | 24
Air Zone | Air Zone | AIRZONE-R3-W1 | 360 | AirZone_Cooling_Capacity | 240 |  |  |  |  | CC-R3 |  |  |  |  | 0 | 300 | 225 | 0 | 0 | 0 | 0 | 300 | 225 | 0 | 0 | 0 | 40 | 30 | 0 | 0 | 0 | 0 | 40 | 30 | 0 | 0 | 27 |  |  |  | 12 | 16.6667 | 24
Air Zone | Air Zone | AIRZONE-R3-W2 | 180 | AirZone_Cooling_Capacity | 180 |  |  |  |  | CC-R3 |  |  |  |  | 0 | 90 | 165 | 0 | 0 | 0 | 0 | 90 | 165 | 0 | 0 | 0 | 12 | 22 | 0 | 0 | 0 | 0 | 12 | 22 | 0 | 0 | 27 |  |  |  | 12 | 12.5 | 24
Air Zone | Air Zone | AIRZONE-R4 | 144 | AirZone_Cooling_Capacity | 180 |  |  |  |  | CC-R4 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 |  |  |  | 12 | 12.5 | 24
Air Zone | Air Zone | AIRZONE-R5-E | 216 | AirZone_Cooling_Capacity | 270 |  |  |  |  | CC-R5E |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 209.25 | 209.25 | 209.25 | 209.25 | 209.25 | 209.25 | 0 | 0 | 0 | 0 | 0 | 24 | 24 | 24 | 24 | 24 | 24 | 27 |  |  |  | 12 | 18.75 | 24
Air Zone | Air Zone | AIRZONE-R5-W | 216 | AirZone_Cooling_Capacity | 270 |  |  |  |  | CC-R5W |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 |  |  |  | 12 | 18.75 | 24
Room PDU | Room PDU | RPDU-R1 | 360 | RPDU_Operational_Cap | 400 | RPDU_Design_Capacity | 480 | RPDU_Transformer_Rating | 600 | [5 empty] | 240 | 0 | 0 | 0 | 0 | 0 | 240 | 240 | 240 | 240 | 240 | 18 | 0 | 0 | 0 | 0 | 0 | 18 | 18 | 18 | 18 | 18
Room PDU | Room PDU | RPDU-R2 | 360 | RPDU_Operational_Cap | 400 | RPDU_Design_Capacity | 480 | RPDU_Transformer_Rating | 600 | [5 empty] | 210 | 0 | 0 | 0 | 0 | 0 | 210 | 210 | 210 | 210 | 210 | 18 | 0 | 0 | 0 | 0 | 0 | 18 | 18 | 18 | 18 | 18
Room PDU | Room PDU | RPDU-R3-A | 5400 | RPDU_Operational_Cap | 4000 | RPDU_Design_Capacity | 4000 | RPDU_Transformer_Rating | 5000 | [5 empty] | 0 | 1560 | 1560 | 1560 | 1560 | 0 | 0 | 1560 | 1560 | 1560 | 1560 | 0 | 52 | 52 | 52 | 52 | 0 | 0 | 52 | 52 | 52 | 52
Room PDU | Room PDU | RPDU-R4-A | 480 | RPDU_Operational_Cap | 2500 | RPDU_Design_Capacity | 3200 | RPDU_Transformer_Rating | 4000 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Room PDU | Room PDU | RPDU-R5-A | 2880 | RPDU_Operational_Cap | 3000 | RPDU_Design_Capacity | 3200 | RPDU_Transformer_Rating | 4000 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 1395 | 1395 | 1395 | 1395 | 1395 | 1395 | 0 | 0 | 0 | 0 | 0 | 24 | 24 | 24 | 24 | 24 | 24
Room PDU | Room PDU | RPDU-R3-B | 1080 | RPDU_Operational_Cap | 960 | RPDU_Design_Capacity | 960 | RPDU_Transformer_Rating | 1200 | [5 empty] | 0 | 780 | 840 | 0 | 0 | 0 | 0 | 780 | 840 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Room PDU | Room PDU | RPDU-R3R4-B | 4800 | RPDU_Operational_Cap | 4000 | RPDU_Design_Capacity | 4000 | RPDU_Transformer_Rating | 5000 | [5 empty] | 0 | 780 | 720 | 1560 | 1560 | 0 | 0 | 780 | 720 | 1560 | 1560 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Room PDU | Room PDU | RPDU-R5-B | 2880 | RPDU_Operational_Cap | 3000 | RPDU_Design_Capacity | 3200 | RPDU_Transformer_Rating | 4000 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 1395 | 1395 | 1395 | 1395 | 1395 | 1395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
UPS | UPS | UPS-01 | 720 | UPS_Operational_Cap | 780 | UPS_Design_Capacity | 800 | UPS_Rated_Capacity | 1000 | [5 empty] | 450 | 0 | 0 | 0 | 0 | 0 | 450 | 450 | 450 | 450 | 450 | 36 | 0 | 0 | 0 | 0 | 0 | 36 | 36 | 36 | 36 | 36
UPS | UPS | UPS-02-A | 8760 | UPS_Operational_Cap | 9000 | UPS_Design_Capacity | 9600 | UPS_Rated_Capacity | 12000 | [5 empty] | 0 | 1560 | 1560 | 1560 | 1560 | 1395 | 1395 | 2955 | 2955 | 2955 | 2955 | 0 | 52 | 52 | 52 | 52 | 24 | 24 | 76 | 76 | 76 | 76
UPS | UPS | UPS-02-B | 8760 | UPS_Operational_Cap | 9000 | UPS_Design_Capacity | 9600 | UPS_Rated_Capacity | 12000 | [5 empty] | 0 | 1560 | 1560 | 1560 | 1560 | 1395 | 1395 | 2955 | 2955 | 2955 | 2955 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cooling Distribution | Cooling Distribution | CDIST-01 | 720 | Cooling_Capacity | 1000 | [9 empty] | 450 | 0 | 0 | 0 | 0 | 0 | 450 | 450 | 450 | 450 | 450 | 72 | 0 | 0 | 0 | 0 | 0 | 72 | 72 | 72 | 72 | 72
Cooling Distribution | Cooling Distribution | CDIST-A-02 | 1602 | Air_Cooling_Capacity | 2000 | [9 empty] | 0 | 1170 | 1170 | 1326 | 1326 | 1185.75 | 1185.75 | 2355.75 | 2355.75 | 2511.75 | 2511.75 | 0 | 52 | 52 | 52 | 52 | 24 | 24 | 76 | 76 | 76 | 76
Cooling Distribution | Cooling Distribution | CDIST-L-02 | 7158 | Liquid_Cooling_Capacity | 7000 | [9 empty] | 0 | 390 | 390 | 234 | 234 | 209.25 | 209.25 | 599.25 | 599.25 | 443.25 | 443.25 | 0 | 52 | 52 | 52 | 52 | 24 | 24 | 76 | 76 | 76 | 76
Capacity Cell | Capacity Cell | CC-R1R2 | 720 | Capacity_Envelope | 920 | [5 empty] | 540 | 400 | 920 |  | 450 | 0 | 0 | 0 | 0 | 0 | 450 | 450 | 450 | 450 | 450 | 36 | 0 | 0 | 0 | 0 | 0 | 36 | 36 | 36 | 36 | 36 | [11 empty] | 940 | 920
Capacity Cell | Capacity Cell | CC-R3 | 5400 | Capacity_Envelope | 3680 | [5 empty] | 840 | 3000 | 3680 | 5060 | 0 | 1560 | 1560 | 1560 | 1560 | 0 | 0 | 1560 | 1560 | 1560 | 1560 | 0 | 52 | 52 | 52 | 52 | 0 | 0 | 52 | 52 | 52 | 52 | [11 empty] | 3840 | 3680
Capacity Cell | Capacity Cell | CC-R4 | 480 | Capacity_Envelope | 680 | [5 empty] | 180 | 500 | 690 | 690 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 680 | 690
Capacity Cell | Capacity Cell | CC-R5E | 1440 | Capacity_Envelope | 1770 | [5 empty] | 270 | 1500 | 1840 | 1840 | 0 | 0 | 0 | 0 | 0 | 1395 | 1395 | 1395 | 1395 | 1395 | 1395 | 0 | 0 | 0 | 0 | 0 | 24 | 24 | 24 | 24 | 24 | 24 | [11 empty] | 1770 | 1840
Capacity Cell | Capacity Cell | CC-R5W | 1440 | Capacity_Envelope | 1770 | [5 empty] | 270 | 1500 | 1840 | 1840 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 1770 | 1840
CDU | CDU | CDU-R1 | [5 empty] | Rated_Cooling_Capacity | 250 | [30 empty] | 6
CDU | CDU | CDU-R2 | [5 empty] | Rated_Cooling_Capacity | 250 | [30 empty] | 6
CDU | CDU | CDU-R3-E | [5 empty] | Rated_Cooling_Capacity | 2200 | [30 empty] | 52
CDU | CDU | CDU-R3-W | [5 empty] | Rated_Cooling_Capacity | 1200 | [30 empty] | 29
CDU | CDU | CDU-R4 | [5 empty] | Rated_Cooling_Capacity | 600 | [30 empty] | 14
CDU | CDU | CDU-R5-W | [5 empty] | Rated_Cooling_Capacity | 1800 | [30 empty] | 43
CDU | CDU | CDU-R5-E | [5 empty] | Rated_Cooling_Capacity | 1800 | [30 empty] | 43
Air Cooling Unit | Air Cooling Unit | CRAH-AZ-R3-E1-01 | [5 empty] | Rated_Cooling_Capacity | 100 | [36 empty] | 6.9444
Air Cooling Unit | Air Cooling Unit | CRAH-AZ-R3-E1-02 | [5 empty] | Rated_Cooling_Capacity | 100 | [36 empty] | 6.9444
Air Cooling Unit | Air Cooling Unit | CRAH-AZ-R3-E1-03 | [5 empty] | Rated_Cooling_Capacity | 100 | [36 empty] | 6.9444
Air Cooling Unit | Air Cooling Unit | CRAH-AZ-R3-E1-04 | [5 empty] | Rated_Cooling_Capacity | 100 | [36 empty] | 6.9444
Air Cooling Unit | Air Cooling Unit | CRAH-AZ-R3-E1-05 | [5 empty] | Rated_Cooling_Capacity | 100 | [36 empty] | 6.9444
Air Cooling Unit | Air Cooling Unit | CRAH-AZ-R3-E2-01 | [5 empty] | Rated_Cooling_Capacity | 100 | [36 empty] | 6.9444
Air Cooling Unit | Air Cooling Unit | CRAH-AZ-R3-E2-02 | [5 empty] | Rated_Cooling_Capacity | 100 | [36 empty] | 6.9444
Air Cooling Unit | Air Cooling Unit | CRAH-AZ-R3-E2-03 | [5 empty] | Rated_Cooling_Capacity | 100 | [36 empty] | 6.9444
Air Cooling Unit | Air Cooling Unit | CRAH-AZ-R3-W1-01 | [5 empty] | Rated_Cooling_Capacity | 100 | [36 empty] | 6.9444
Air Cooling Unit | Air Cooling Unit | CRAH-AZ-R3-W1-02 | [5 empty] | Rated_Cooling_Capacity | 100 | [36 empty] | 6.9444
Air Cooling Unit | Air Cooling Unit | CRAH-AZ-R3-W1-03 | [5 empty] | Rated_Cooling_Capacity | 100 | [36 empty] | 6.9444
Air Cooling Unit | Air Cooling Unit | CRAH-AZ-R3-W1-04 | [5 empty] | Rated_Cooling_Capacity | 100 | [36 empty] | 6.9444
Air Cooling Unit | Air Cooling Unit | CRAH-AZ-R3-W1-05 | [5 empty] | Rated_Cooling_Capacity | 100 | [36 empty] | 6.9444
Air Cooling Unit | Air Cooling Unit | CRAH-AZ-R3-W2-01 | [5 empty] | Rated_Cooling_Capacity | 100 | [36 empty] | 6.9444
Air Cooling Unit | Air Cooling Unit | CRAH-AZ-R3-W2-02 | [5 empty] | Rated_Cooling_Capacity | 100 | [36 empty] | 6.9444
Air Cooling Unit | Air Cooling Unit | CRAH-AZ-R3-W2-03 | [5 empty] | Rated_Cooling_Capacity | 100 | [36 empty] | 6.9444
Air Cooling Unit | Air Cooling Unit | CRAH-AZ-R4-01 | [5 empty] | Rated_Cooling_Capacity | 100 | [36 empty] | 6.9444
Air Cooling Unit | Air Cooling Unit | CRAH-AZ-R4-02 | [5 empty] | Rated_Cooling_Capacity | 100 | [36 empty] | 6.9444
Air Cooling Unit | Air Cooling Unit | CRAH-AZ-R4-03 | [5 empty] | Rated_Cooling_Capacity | 100 | [36 empty] | 6.9444
Air Cooling Unit | Air Cooling Unit | CRAH-AZ-R5-W-01 | [5 empty] | Rated_Cooling_Capacity | 100 | [36 empty] | 6.9444
Air Cooling Unit | Air Cooling Unit | CRAH-AZ-R5-W-02 | [5 empty] | Rated_Cooling_Capacity | 100 | [36 empty] | 6.9444
Air Cooling Unit | Air Cooling Unit | CRAH-AZ-R5-W-03 | [5 empty] | Rated_Cooling_Capacity | 100 | [36 empty] | 6.9444
Air Cooling Unit | Air Cooling Unit | CRAH-AZ-R5-W-04 | [5 empty] | Rated_Cooling_Capacity | 100 | [36 empty] | 6.9444
Air Cooling Unit | Air Cooling Unit | CRAH-AZ-R5-E-05 | [5 empty] | Rated_Cooling_Capacity | 100 | [36 empty] | 6.9444
Air Cooling Unit | Air Cooling Unit | CRAH-AZ-R5-E-06 | [5 empty] | Rated_Cooling_Capacity | 100 | [36 empty] | 6.9444
Air Cooling Unit | Air Cooling Unit | CRAH-AZ-R5-E-07 | [5 empty] | Rated_Cooling_Capacity | 100 | [36 empty] | 6.9444
Air Cooling Unit | Air Cooling Unit | CRAH-AZ-R5-E-08 | [5 empty] | Rated_Cooling_Capacity | 100 | [36 empty] | 6.9444

## Upstream
Rack | RPP(A) | RPP(B) | Room PDU (A) | Room PDU (B) | UPS (A) | UPS (B) | Utility Feed (A) | Utility Feed (B) | Air Zone | Liquid Loop | Cooling Distribution (Combined) | Cooling Distribution (Air) | Cooling Distribution (Liquid) | Capacity Cell | Room Bundle | Room PDU Bundle | UPS Bundle
RACK-R1-Z1-R1-01 | RPP-R1-1 | (blank) | RPDU-R1 | (blank) | UPS-01 | (blank) | UTIL-01 | UTIL-02 | AIRZONE-R1 | LL-R1 | CDIST-01 |  |  | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01
RACK-R1-Z1-R1-02 | RPP-R1-2 | (blank) | RPDU-R1 | (blank) | UPS-01 | (blank) | UTIL-01 | UTIL-02 | AIRZONE-R1 | LL-R1 | CDIST-01 |  |  | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01
RACK-R1-Z1-R1-03 | RPP-R2-1 | (blank) | RPDU-R2 | (blank) | UPS-01 | (blank) | UTIL-01 | UTIL-02 | AIRZONE-R1 | LL-R1 | CDIST-01 |  |  | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01
RACK-R1-Z1-R1-04 | RPP-R2-2 | (blank) | RPDU-R2 | (blank) | UPS-01 | (blank) | UTIL-01 | UTIL-02 | AIRZONE-R1 | LL-R1 | CDIST-01 |  |  | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01
RACK-R1-Z1-R1-05 | RPP-R1-1 | (blank) | RPDU-R1 | (blank) | UPS-01 | (blank) | UTIL-01 | UTIL-02 | AIRZONE-R1 | LL-R1 | CDIST-01 |  |  | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01
RACK-R1-Z1-R1-06 | RPP-R1-2 | (blank) | RPDU-R1 | (blank) | UPS-01 | (blank) | UTIL-01 | UTIL-02 | AIRZONE-R1 | LL-R1 | CDIST-01 |  |  | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01
RACK-R1-Z1-R2-01 | RPP-R2-1 | (blank) | RPDU-R2 | (blank) | UPS-01 | (blank) | UTIL-01 | UTIL-02 | AIRZONE-R1 | LL-R1 | CDIST-01 |  |  | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01
RACK-R1-Z1-R2-02 | RPP-R2-2 | (blank) | RPDU-R2 | (blank) | UPS-01 | (blank) | UTIL-01 | UTIL-02 | AIRZONE-R1 | LL-R1 | CDIST-01 |  |  | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01
RACK-R1-Z1-R2-03 | RPP-R1-1 | (blank) | RPDU-R1 | (blank) | UPS-01 | (blank) | UTIL-01 | UTIL-02 | AIRZONE-R1 | LL-R1 | CDIST-01 |  |  | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01
RACK-R1-Z1-R2-04 | RPP-R1-2 | (blank) | RPDU-R1 | (blank) | UPS-01 | (blank) | UTIL-01 | UTIL-02 | AIRZONE-R1 | LL-R1 | CDIST-01 |  |  | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01
RACK-R1-Z1-R2-05 | RPP-R2-1 | (blank) | RPDU-R2 | (blank) | UPS-01 | (blank) | UTIL-01 | UTIL-02 | AIRZONE-R1 | LL-R1 | CDIST-01 |  |  | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01
RACK-R1-Z1-R2-06 | RPP-R2-2 | (blank) | RPDU-R2 | (blank) | UPS-01 | (blank) | UTIL-01 | UTIL-02 | AIRZONE-R1 | LL-R1 | CDIST-01 |  |  | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01
RACK-R1-Z2-R1-01 | RPP-R1-1 | (blank) | RPDU-R1 | (blank) | UPS-01 | (blank) | UTIL-01 | UTIL-02 | AIRZONE-R1 | LL-R1 | CDIST-01 |  |  | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01
RACK-R1-Z2-R1-02 | RPP-R1-2 | (blank) | RPDU-R1 | (blank) | UPS-01 | (blank) | UTIL-01 | UTIL-02 | AIRZONE-R1 | LL-R1 | CDIST-01 |  |  | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01
RACK-R1-Z2-R1-03 | RPP-R2-1 | (blank) | RPDU-R2 | (blank) | UPS-01 | (blank) | UTIL-01 | UTIL-02 | AIRZONE-R1 | LL-R1 | CDIST-01 |  |  | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01
RACK-R1-Z2-R1-04 | RPP-R2-2 | (blank) | RPDU-R2 | (blank) | UPS-01 | (blank) | UTIL-01 | UTIL-02 | AIRZONE-R1 | LL-R1 | CDIST-01 |  |  | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01
RACK-R1-Z2-R1-05 | RPP-R1-1 | (blank) | RPDU-R1 | (blank) | UPS-01 | (blank) | UTIL-01 | UTIL-02 | AIRZONE-R1 | LL-R1 | CDIST-01 |  |  | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01
RACK-R1-Z2-R1-06 | RPP-R1-2 | (blank) | RPDU-R1 | (blank) | UPS-01 | (blank) | UTIL-01 | UTIL-02 | AIRZONE-R1 | LL-R1 | CDIST-01 |  |  | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01
RACK-R1-Z2-R2-01 | RPP-R2-1 | (blank) | RPDU-R2 | (blank) | UPS-01 | (blank) | UTIL-01 | UTIL-02 | AIRZONE-R1 | LL-R1 | CDIST-01 |  |  | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01
RACK-R1-Z2-R2-02 | RPP-R2-2 | (blank) | RPDU-R2 | (blank) | UPS-01 | (blank) | UTIL-01 | UTIL-02 | AIRZONE-R1 | LL-R1 | CDIST-01 |  |  | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01
RACK-R1-Z2-R2-03 | RPP-R1-1 | (blank) | RPDU-R1 | (blank) | UPS-01 | (blank) | UTIL-01 | UTIL-02 | AIRZONE-R1 | LL-R1 | CDIST-01 |  |  | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01
RACK-R1-Z2-R2-04 | RPP-R1-2 | (blank) | RPDU-R1 | (blank) | UPS-01 | (blank) | UTIL-01 | UTIL-02 | AIRZONE-R1 | LL-R1 | CDIST-01 |  |  | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01
RACK-R1-Z2-R2-05 | RPP-R2-1 | (blank) | RPDU-R2 | (blank) | UPS-01 | (blank) | UTIL-01 | UTIL-02 | AIRZONE-R1 | LL-R1 | CDIST-01 |  |  | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01
RACK-R1-Z2-R2-06 | RPP-R2-2 | (blank) | RPDU-R2 | (blank) | UPS-01 | (blank) | UTIL-01 | UTIL-02 | AIRZONE-R1 | LL-R1 | CDIST-01 |  |  | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01
RACK-R2-Z1-R1-01 | RPP-R1-1 | (blank) | RPDU-R1 | (blank) | UPS-01 | (blank) | UTIL-01 | UTIL-02 | AIRZONE-R2 | LL-R2 | CDIST-01 |  |  | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01
RACK-R2-Z1-R1-02 | RPP-R1-2 | (blank) | RPDU-R1 | (blank) | UPS-01 | (blank) | UTIL-01 | UTIL-02 | AIRZONE-R2 | LL-R2 | CDIST-01 |  |  | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01
RACK-R2-Z1-R1-03 | RPP-R2-1 | (blank) | RPDU-R2 | (blank) | UPS-01 | (blank) | UTIL-01 | UTIL-02 | AIRZONE-R2 | LL-R2 | CDIST-01 |  |  | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01
RACK-R2-Z1-R1-04 | RPP-R2-2 | (blank) | RPDU-R2 | (blank) | UPS-01 | (blank) | UTIL-01 | UTIL-02 | AIRZONE-R2 | LL-R2 | CDIST-01 |  |  | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01
RACK-R2-Z1-R1-05 | RPP-R1-1 | (blank) | RPDU-R1 | (blank) | UPS-01 | (blank) | UTIL-01 | UTIL-02 | AIRZONE-R2 | LL-R2 | CDIST-01 |  |  | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01
RACK-R2-Z1-R1-06 | RPP-R1-2 | (blank) | RPDU-R1 | (blank) | UPS-01 | (blank) | UTIL-01 | UTIL-02 | AIRZONE-R2 | LL-R2 | CDIST-01 |  |  | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01
RACK-R2-Z1-R2-01 | RPP-R2-1 | (blank) | RPDU-R2 | (blank) | UPS-01 | (blank) | UTIL-01 | UTIL-02 | AIRZONE-R2 | LL-R2 | CDIST-01 |  |  | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01
RACK-R2-Z1-R2-02 | RPP-R2-2 | (blank) | RPDU-R2 | (blank) | UPS-01 | (blank) | UTIL-01 | UTIL-02 | AIRZONE-R2 | LL-R2 | CDIST-01 |  |  | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01
RACK-R2-Z1-R2-03 | RPP-R1-1 | (blank) | RPDU-R1 | (blank) | UPS-01 | (blank) | UTIL-01 | UTIL-02 | AIRZONE-R2 | LL-R2 | CDIST-01 |  |  | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01
RACK-R2-Z1-R2-04 | RPP-R1-2 | (blank) | RPDU-R1 | (blank) | UPS-01 | (blank) | UTIL-01 | UTIL-02 | AIRZONE-R2 | LL-R2 | CDIST-01 |  |  | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01
RACK-R2-Z1-R2-05 | RPP-R2-1 | (blank) | RPDU-R2 | (blank) | UPS-01 | (blank) | UTIL-01 | UTIL-02 | AIRZONE-R2 | LL-R2 | CDIST-01 |  |  | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01
RACK-R2-Z1-R2-06 | RPP-R2-2 | (blank) | RPDU-R2 | (blank) | UPS-01 | (blank) | UTIL-01 | UTIL-02 | AIRZONE-R2 | LL-R2 | CDIST-01 |  |  | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01
RACK-R2-Z2-R1-01 | RPP-R1-1 | (blank) | RPDU-R1 | (blank) | UPS-01 | (blank) | UTIL-01 | UTIL-02 | AIRZONE-R2 | LL-R2 | CDIST-01 |  |  | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01
RACK-R2-Z2-R1-02 | RPP-R1-2 | (blank) | RPDU-R1 | (blank) | UPS-01 | (blank) | UTIL-01 | UTIL-02 | AIRZONE-R2 | LL-R2 | CDIST-01 |  |  | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01
RACK-R2-Z2-R1-03 | RPP-R2-1 | (blank) | RPDU-R2 | (blank) | UPS-01 | (blank) | UTIL-01 | UTIL-02 | AIRZONE-R2 | LL-R2 | CDIST-01 |  |  | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01
RACK-R2-Z2-R1-04 | RPP-R2-2 | (blank) | RPDU-R2 | (blank) | UPS-01 | (blank) | UTIL-01 | UTIL-02 | AIRZONE-R2 | LL-R2 | CDIST-01 |  |  | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01
RACK-R2-Z2-R1-05 | RPP-R1-1 | (blank) | RPDU-R1 | (blank) | UPS-01 | (blank) | UTIL-01 | UTIL-02 | AIRZONE-R2 | LL-R2 | CDIST-01 |  |  | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01
RACK-R2-Z2-R1-06 | RPP-R1-2 | (blank) | RPDU-R1 | (blank) | UPS-01 | (blank) | UTIL-01 | UTIL-02 | AIRZONE-R2 | LL-R2 | CDIST-01 |  |  | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01
RACK-R2-Z2-R2-01 | RPP-R2-1 | (blank) | RPDU-R2 | (blank) | UPS-01 | (blank) | UTIL-01 | UTIL-02 | AIRZONE-R2 | LL-R2 | CDIST-01 |  |  | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01
RACK-R2-Z2-R2-02 | RPP-R2-2 | (blank) | RPDU-R2 | (blank) | UPS-01 | (blank) | UTIL-01 | UTIL-02 | AIRZONE-R2 | LL-R2 | CDIST-01 |  |  | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01
RACK-R2-Z2-R2-03 | RPP-R1-1 | (blank) | RPDU-R1 | (blank) | UPS-01 | (blank) | UTIL-01 | UTIL-02 | AIRZONE-R2 | LL-R2 | CDIST-01 |  |  | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01
RACK-R2-Z2-R2-04 | RPP-R1-2 | (blank) | RPDU-R1 | (blank) | UPS-01 | (blank) | UTIL-01 | UTIL-02 | AIRZONE-R2 | LL-R2 | CDIST-01 |  |  | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01
RACK-R2-Z2-R2-05 | RPP-R2-1 | (blank) | RPDU-R2 | (blank) | UPS-01 | (blank) | UTIL-01 | UTIL-02 | AIRZONE-R2 | LL-R2 | CDIST-01 |  |  | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01
RACK-R2-Z2-R2-06 | RPP-R2-2 | (blank) | RPDU-R2 | (blank) | UPS-01 | (blank) | UTIL-01 | UTIL-02 | AIRZONE-R2 | LL-R2 | CDIST-01 |  |  | CC-R1R2 | BDL-R1R2 | BDL-RPDU-R1R2 | BDL-UPS-01
RACK-R3-Z1W-R1-01 | RPP-R3-A1 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-W1 | LL-R3-W |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z1W-R1-02 | RPP-R3-A1 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-W1 | LL-R3-W |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z1W-R1-03 | RPP-R3-A1 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-W1 | LL-R3-W |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z1W-R1-04 | RPP-R3-A1 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-W1 | LL-R3-W |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z1W-R1-05 | RPP-R3-A2 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-W1 | LL-R3-W |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z1W-R1-06 | RPP-R3-A2 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-W1 | LL-R3-W |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z1W-R1-07 | RPP-R3-A2 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-W1 | LL-R3-W |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z1W-R1-08 | RPP-R3-A2 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-W1 | LL-R3-W |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z1W-R1-09 | RPP-R3-A1 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-W1 | LL-R3-W |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z1W-R1-10 | RPP-R3-A1 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-W1 | LL-R3-W |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z1W-R1-11 | RPP-R3-A1 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-W1 | LL-R3-W |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z1W-R1-12 | RPP-R3-A1 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-W1 | LL-R3-W |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z1W-R2-01 | RPP-R3-A2 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-W1 | LL-R3-W |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z1W-R2-02 | RPP-R3-A2 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-W1 | LL-R3-W |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z1W-R2-03 | RPP-R3-A2 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-W1 | LL-R3-W |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z1W-R2-04 | RPP-R3-A2 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-W1 | LL-R3-W |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z1W-R2-05 | RPP-R3-A1 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-W1 | LL-R3-W |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z1W-R2-06 | RPP-R3-A1 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-W1 | LL-R3-W |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z1W-R2-07 | RPP-R3-A1 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-W1 | LL-R3-W |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z1W-R2-08 | RPP-R3-A1 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-W1 | LL-R3-W |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z1W-R2-09 | RPP-R3-A2 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-W1 | LL-R3-W |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z1W-R2-10 | RPP-R3-A2 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-W1 | LL-R3-W |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z1W-R2-11 | RPP-R3-A2 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-W1 | LL-R3-W |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z1W-R2-12 | RPP-R3-A2 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-W1 | LL-R3-W |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z2W-R1-01 | RPP-R3-A1 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-W1 | LL-R3-W |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z2W-R1-02 | RPP-R3-A1 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-W1 | LL-R3-W |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z2W-R1-03 | RPP-R3-A1 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-W1 | LL-R3-W |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z2W-R1-04 | RPP-R3-A1 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-W1 | LL-R3-W |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z2W-R1-05 | RPP-R3-A2 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-W1 | LL-R3-W |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z2W-R1-06 | RPP-R3-A2 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-W1 | LL-R3-W |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z2W-R1-07 | RPP-R3-A2 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-W1 | LL-R3-W |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z2W-R1-08 | RPP-R3-A2 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-W1 | LL-R3-W |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z2W-R1-09 | RPP-R3-A1 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-W1 | LL-R3-W |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z2W-R1-10 | RPP-R3-A1 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-W1 | LL-R3-W |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z2W-R1-11 | RPP-R3-A1 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-W1 | LL-R3-W |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z2W-R1-12 | RPP-R3-A1 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-W1 | LL-R3-W |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z2W-R2-01 | RPP-R3-A2 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-W1 | LL-R3-W |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z2W-R2-02 | RPP-R3-A2 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-W1 | LL-R3-W |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z2W-R2-03 | RPP-R3-A2 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-W1 | LL-R3-W |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z2W-R2-04 | RPP-R3-A2 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-W1 | LL-R3-W |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z2W-R2-05 | RPP-R3-A1 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-W1 | LL-R3-W |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z2W-R2-06 | RPP-R3-A1 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-W1 | LL-R3-W |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z2W-R2-07 | RPP-R3-A1 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-W1 | LL-R3-W |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z2W-R2-08 | RPP-R3-A1 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-W1 | LL-R3-W |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z2W-R2-09 | RPP-R3-A2 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-W1 | LL-R3-W |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z2W-R2-10 | RPP-R3-A2 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-W1 | LL-R3-W |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z2W-R2-11 | RPP-R3-A2 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-W1 | LL-R3-W |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z2W-R2-12 | RPP-R3-A2 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-W1 | LL-R3-W |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z3W-R1-01 | RPP-R3-A1 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-W2 | LL-R3-W |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z3W-R1-02 | RPP-R3-A1 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-W2 | LL-R3-W |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z3W-R1-03 | RPP-R3-A1 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-W2 | LL-R3-W |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z3W-R1-04 | RPP-R3-A1 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-W2 | LL-R3-W |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z3W-R1-05 | RPP-R3-A2 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-W2 | LL-R3-W |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z3W-R1-06 | RPP-R3-A2 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-W2 | LL-R3-W |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z3W-R1-07 | RPP-R3-A2 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-W2 | LL-R3-W |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z3W-R1-08 | RPP-R3-A2 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-W2 | LL-R3-W |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z3W-R1-09 | RPP-R3-A1 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-W2 | LL-R3-W |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z3W-R1-10 | RPP-R3-A1 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-W2 | LL-R3-W |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z3W-R1-11 | RPP-R3-A1 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-W2 | LL-R3-W |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z3W-R1-12 | RPP-R3-A1 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-W2 | LL-R3-W |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z3W-R2-01 | RPP-R3-A2 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-W2 | LL-R3-W |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z3W-R2-02 | RPP-R3-A2 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-W2 | LL-R3-W |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z3W-R2-03 | RPP-R3-A2 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-W2 | LL-R3-W |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z3W-R2-04 | RPP-R3-A2 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-W2 | LL-R3-W |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z3W-R2-05 | RPP-R3-A1 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-W2 | LL-R3-W |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z3W-R2-06 | RPP-R3-A1 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-W2 | LL-R3-W |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z3W-R2-07 | RPP-R3-A1 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-W2 | LL-R3-W |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z3W-R2-08 | RPP-R3-A1 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-W2 | LL-R3-W |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z3W-R2-09 | RPP-R3-A2 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-W2 | LL-R3-W |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z3W-R2-10 | RPP-R3-A2 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-W2 | LL-R3-W |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z3W-R2-11 | RPP-R3-A2 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-W2 | LL-R3-W |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z3W-R2-12 | RPP-R3-A2 | RPP-R3-B3 | RPDU-R3-A | RPDU-R3-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-W2 | LL-R3-W |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z4E-R1-01 | RPP-R3-A1 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-E1 | LL-R3-E |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z4E-R1-02 | RPP-R3-A1 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-E1 | LL-R3-E |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z4E-R1-03 | RPP-R3-A1 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-E1 | LL-R3-E |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z4E-R1-04 | RPP-R3-A1 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-E1 | LL-R3-E |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z4E-R1-05 | RPP-R3-A3 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-E1 | LL-R3-E |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z4E-R1-06 | RPP-R3-A3 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-E1 | LL-R3-E |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z4E-R1-07 | RPP-R3-A3 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-E1 | LL-R3-E |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z4E-R1-08 | RPP-R3-A3 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-E1 | LL-R3-E |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z4E-R1-09 | RPP-R3-A3 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-E1 | LL-R3-E |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z4E-R1-10 | RPP-R3-A3 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-E1 | LL-R3-E |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z4E-R1-11 | RPP-R3-A3 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-E1 | LL-R3-E |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z4E-R1-12 | RPP-R3-A3 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-E1 | LL-R3-E |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z4E-R2-01 | RPP-R3-A2 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-E1 | LL-R3-E |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z4E-R2-02 | RPP-R3-A2 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-E1 | LL-R3-E |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z4E-R2-03 | RPP-R3-A2 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-E1 | LL-R3-E |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z4E-R2-04 | RPP-R3-A2 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-E1 | LL-R3-E |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z4E-R2-05 | RPP-R3-A4 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-E1 | LL-R3-E |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z4E-R2-06 | RPP-R3-A4 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-E1 | LL-R3-E |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z4E-R2-07 | RPP-R3-A4 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-E1 | LL-R3-E |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z4E-R2-08 | RPP-R3-A4 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-E1 | LL-R3-E |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z4E-R2-09 | RPP-R3-A4 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-E1 | LL-R3-E |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z4E-R2-10 | RPP-R3-A4 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-E1 | LL-R3-E |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z4E-R2-11 | RPP-R3-A4 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-E1 | LL-R3-E |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z4E-R2-12 | RPP-R3-A4 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-E1 | LL-R3-E |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z5E-R1-01 | RPP-R3-A3 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-E1 | LL-R3-E |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z5E-R1-02 | RPP-R3-A4 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-E1 | LL-R3-E |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z5E-R1-03 | RPP-R3-A3 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-E1 | LL-R3-E |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z5E-R1-04 | RPP-R3-A4 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-E1 | LL-R3-E |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z5E-R1-05 | RPP-R3-A3 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-E1 | LL-R3-E |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z5E-R1-06 | RPP-R3-A4 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-E1 | LL-R3-E |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z5E-R1-07 | RPP-R3-A3 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-E1 | LL-R3-E |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z5E-R1-08 | RPP-R3-A4 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-E1 | LL-R3-E |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z5E-R1-09 | RPP-R3-A3 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-E1 | LL-R3-E |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z5E-R1-10 | RPP-R3-A4 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-E1 | LL-R3-E |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z5E-R1-11 | RPP-R3-A3 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-E1 | LL-R3-E |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z5E-R1-12 | RPP-R3-A4 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-E1 | LL-R3-E |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z5E-R2-01 | RPP-R3-A3 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-E1 | LL-R3-E |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z5E-R2-02 | RPP-R3-A4 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-E1 | LL-R3-E |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z5E-R2-03 | RPP-R3-A3 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-E1 | LL-R3-E |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z5E-R2-04 | RPP-R3-A4 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-E1 | LL-R3-E |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z5E-R2-05 | RPP-R3-A3 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-E1 | LL-R3-E |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z5E-R2-06 | RPP-R3-A4 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-E1 | LL-R3-E |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z5E-R2-07 | RPP-R3-A3 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-E1 | LL-R3-E |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z5E-R2-08 | RPP-R3-A4 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-E1 | LL-R3-E |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z5E-R2-09 | RPP-R3-A3 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-E1 | LL-R3-E |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z5E-R2-10 | RPP-R3-A4 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-E1 | LL-R3-E |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z5E-R2-11 | RPP-R3-A3 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-E1 | LL-R3-E |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z5E-R2-12 | RPP-R3-A4 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-E1 | LL-R3-E |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z6E-R1-01 | RPP-R3-A3 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-E2 | LL-R3-E |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z6E-R1-02 | RPP-R3-A4 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-E2 | LL-R3-E |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z6E-R1-03 | RPP-R3-A3 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-E2 | LL-R3-E |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z6E-R1-04 | RPP-R3-A4 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-E2 | LL-R3-E |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z6E-R1-05 | RPP-R3-A3 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-E2 | LL-R3-E |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z6E-R1-06 | RPP-R3-A4 | RPP-R3-B1 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-E2 | LL-R3-E |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z6E-R1-07 | RPP-R3-A3 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-E2 | LL-R3-E |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z6E-R1-08 | RPP-R3-A4 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-E2 | LL-R3-E |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z6E-R1-09 | RPP-R3-A3 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-E2 | LL-R3-E |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z6E-R1-10 | RPP-R3-A4 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-E2 | LL-R3-E |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z6E-R1-11 | RPP-R3-A3 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-E2 | LL-R3-E |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z6E-R1-12 | RPP-R3-A4 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-E2 | LL-R3-E |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z6E-R2-01 | RPP-R3-A3 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-E2 | LL-R3-E |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z6E-R2-02 | RPP-R3-A4 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-E2 | LL-R3-E |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z6E-R2-03 | RPP-R3-A3 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-E2 | LL-R3-E |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z6E-R2-04 | RPP-R3-A4 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-E2 | LL-R3-E |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z6E-R2-05 | RPP-R3-A3 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-E2 | LL-R3-E |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z6E-R2-06 | RPP-R3-A4 | RPP-R3-B2 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-E2 | LL-R3-E |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z6E-R2-07 | RPP-R3-A3 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-E2 | LL-R3-E |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z6E-R2-08 | RPP-R3-A4 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-E2 | LL-R3-E |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z6E-R2-09 | RPP-R3-A3 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-E2 | LL-R3-E |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z6E-R2-10 | RPP-R3-A4 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-E2 | LL-R3-E |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z6E-R2-11 | RPP-R3-A3 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-E2 | LL-R3-E |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R3-Z6E-R2-12 | RPP-R3-A4 | RPP-R3-B4 | RPDU-R3-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R3-E2 | LL-R3-E |  | CDIST-A-02 | CDIST-L-02 | CC-R3 | BDL-R3 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R4-Z1-R1-01 | RPP-R4-A5 | RPP-R4-B5 | RPDU-R4-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R4 | LL-R4 |  | CDIST-A-02 | CDIST-L-02 | CC-R4 | BDL-R4 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R4-Z1-R1-02 | RPP-R4-A6 | RPP-R4-B6 | RPDU-R4-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R4 | LL-R4 |  | CDIST-A-02 | CDIST-L-02 | CC-R4 | BDL-R4 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R4-Z1-R1-03 | RPP-R4-A5 | RPP-R4-B5 | RPDU-R4-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R4 | LL-R4 |  | CDIST-A-02 | CDIST-L-02 | CC-R4 | BDL-R4 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R4-Z1-R1-04 | RPP-R4-A6 | RPP-R4-B6 | RPDU-R4-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R4 | LL-R4 |  | CDIST-A-02 | CDIST-L-02 | CC-R4 | BDL-R4 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R4-Z1-R1-05 | RPP-R4-A5 | RPP-R4-B5 | RPDU-R4-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R4 | LL-R4 |  | CDIST-A-02 | CDIST-L-02 | CC-R4 | BDL-R4 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R4-Z1-R1-06 | RPP-R4-A6 | RPP-R4-B6 | RPDU-R4-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R4 | LL-R4 |  | CDIST-A-02 | CDIST-L-02 | CC-R4 | BDL-R4 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R4-Z1-R1-07 | RPP-R4-A5 | RPP-R4-B5 | RPDU-R4-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R4 | LL-R4 |  | CDIST-A-02 | CDIST-L-02 | CC-R4 | BDL-R4 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R4-Z1-R1-08 | RPP-R4-A6 | RPP-R4-B6 | RPDU-R4-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R4 | LL-R4 |  | CDIST-A-02 | CDIST-L-02 | CC-R4 | BDL-R4 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R4-Z1-R1-09 | RPP-R4-A5 | RPP-R4-B5 | RPDU-R4-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R4 | LL-R4 |  | CDIST-A-02 | CDIST-L-02 | CC-R4 | BDL-R4 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R4-Z1-R1-10 | RPP-R4-A6 | RPP-R4-B6 | RPDU-R4-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R4 | LL-R4 |  | CDIST-A-02 | CDIST-L-02 | CC-R4 | BDL-R4 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R4-Z1-R1-11 | RPP-R4-A5 | RPP-R4-B5 | RPDU-R4-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R4 | LL-R4 |  | CDIST-A-02 | CDIST-L-02 | CC-R4 | BDL-R4 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R4-Z1-R1-12 | RPP-R4-A6 | RPP-R4-B6 | RPDU-R4-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R4 | LL-R4 |  | CDIST-A-02 | CDIST-L-02 | CC-R4 | BDL-R4 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R4-Z1-R2-01 | RPP-R4-A5 | RPP-R4-B5 | RPDU-R4-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R4 | LL-R4 |  | CDIST-A-02 | CDIST-L-02 | CC-R4 | BDL-R4 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R4-Z1-R2-02 | RPP-R4-A6 | RPP-R4-B6 | RPDU-R4-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R4 | LL-R4 |  | CDIST-A-02 | CDIST-L-02 | CC-R4 | BDL-R4 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R4-Z1-R2-03 | RPP-R4-A5 | RPP-R4-B5 | RPDU-R4-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R4 | LL-R4 |  | CDIST-A-02 | CDIST-L-02 | CC-R4 | BDL-R4 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R4-Z1-R2-04 | RPP-R4-A6 | RPP-R4-B6 | RPDU-R4-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R4 | LL-R4 |  | CDIST-A-02 | CDIST-L-02 | CC-R4 | BDL-R4 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R4-Z1-R2-05 | RPP-R4-A5 | RPP-R4-B5 | RPDU-R4-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R4 | LL-R4 |  | CDIST-A-02 | CDIST-L-02 | CC-R4 | BDL-R4 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R4-Z1-R2-06 | RPP-R4-A6 | RPP-R4-B6 | RPDU-R4-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R4 | LL-R4 |  | CDIST-A-02 | CDIST-L-02 | CC-R4 | BDL-R4 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R4-Z1-R2-07 | RPP-R4-A5 | RPP-R4-B5 | RPDU-R4-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R4 | LL-R4 |  | CDIST-A-02 | CDIST-L-02 | CC-R4 | BDL-R4 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R4-Z1-R2-08 | RPP-R4-A6 | RPP-R4-B6 | RPDU-R4-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R4 | LL-R4 |  | CDIST-A-02 | CDIST-L-02 | CC-R4 | BDL-R4 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R4-Z1-R2-09 | RPP-R4-A5 | RPP-R4-B5 | RPDU-R4-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R4 | LL-R4 |  | CDIST-A-02 | CDIST-L-02 | CC-R4 | BDL-R4 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R4-Z1-R2-10 | RPP-R4-A6 | RPP-R4-B6 | RPDU-R4-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R4 | LL-R4 |  | CDIST-A-02 | CDIST-L-02 | CC-R4 | BDL-R4 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R4-Z1-R2-11 | RPP-R4-A5 | RPP-R4-B5 | RPDU-R4-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R4 | LL-R4 |  | CDIST-A-02 | CDIST-L-02 | CC-R4 | BDL-R4 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R4-Z1-R2-12 | RPP-R4-A6 | RPP-R4-B6 | RPDU-R4-A | RPDU-R3R4-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R4 | LL-R4 |  | CDIST-A-02 | CDIST-L-02 | CC-R4 | BDL-R4 | BDL-RPDU-R3R4 | BDL-UPS-02
RACK-R5-Z1W-R1-01 | RPP-R5-A1 | RPP-R5-B1 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R5-W | LL-R5-W |  | CDIST-A-02 | CDIST-L-02 | CC-R5W | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02
RACK-R5-Z1W-R1-02 | RPP-R5-A1 | RPP-R5-B1 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R5-W | LL-R5-W |  | CDIST-A-02 | CDIST-L-02 | CC-R5W | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02
RACK-R5-Z1W-R1-03 | RPP-R5-A1 | RPP-R5-B1 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R5-W | LL-R5-W |  | CDIST-A-02 | CDIST-L-02 | CC-R5W | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02
RACK-R5-Z1W-R1-04 | RPP-R5-A1 | RPP-R5-B1 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R5-W | LL-R5-W |  | CDIST-A-02 | CDIST-L-02 | CC-R5W | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02
RACK-R5-Z1W-R1-05 | RPP-R5-A1 | RPP-R5-B1 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R5-W | LL-R5-W |  | CDIST-A-02 | CDIST-L-02 | CC-R5W | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02
RACK-R5-Z1W-R1-06 | RPP-R5-A1 | RPP-R5-B1 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R5-W | LL-R5-W |  | CDIST-A-02 | CDIST-L-02 | CC-R5W | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02
RACK-R5-Z1W-R1-07 | RPP-R5-A1 | RPP-R5-B1 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R5-W | LL-R5-W |  | CDIST-A-02 | CDIST-L-02 | CC-R5W | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02
RACK-R5-Z1W-R1-08 | RPP-R5-A1 | RPP-R5-B1 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R5-W | LL-R5-W |  | CDIST-A-02 | CDIST-L-02 | CC-R5W | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02
RACK-R5-Z1W-R1-09 | RPP-R5-A1 | RPP-R5-B1 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R5-W | LL-R5-W |  | CDIST-A-02 | CDIST-L-02 | CC-R5W | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02
RACK-R5-Z1W-R1-10 | RPP-R5-A1 | RPP-R5-B1 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R5-W | LL-R5-W |  | CDIST-A-02 | CDIST-L-02 | CC-R5W | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02
RACK-R5-Z1W-R1-11 | RPP-R5-A1 | RPP-R5-B1 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R5-W | LL-R5-W |  | CDIST-A-02 | CDIST-L-02 | CC-R5W | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02
RACK-R5-Z1W-R1-12 | RPP-R5-A1 | RPP-R5-B1 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R5-W | LL-R5-W |  | CDIST-A-02 | CDIST-L-02 | CC-R5W | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02
RACK-R5-Z1W-R2-01 | RPP-R5-A2 | RPP-R5-B2 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R5-W | LL-R5-W |  | CDIST-A-02 | CDIST-L-02 | CC-R5W | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02
RACK-R5-Z1W-R2-02 | RPP-R5-A2 | RPP-R5-B2 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R5-W | LL-R5-W |  | CDIST-A-02 | CDIST-L-02 | CC-R5W | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02
RACK-R5-Z1W-R2-03 | RPP-R5-A2 | RPP-R5-B2 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R5-W | LL-R5-W |  | CDIST-A-02 | CDIST-L-02 | CC-R5W | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02
RACK-R5-Z1W-R2-04 | RPP-R5-A2 | RPP-R5-B2 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R5-W | LL-R5-W |  | CDIST-A-02 | CDIST-L-02 | CC-R5W | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02
RACK-R5-Z1W-R2-05 | RPP-R5-A2 | RPP-R5-B2 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R5-W | LL-R5-W |  | CDIST-A-02 | CDIST-L-02 | CC-R5W | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02
RACK-R5-Z1W-R2-06 | RPP-R5-A2 | RPP-R5-B2 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R5-W | LL-R5-W |  | CDIST-A-02 | CDIST-L-02 | CC-R5W | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02
RACK-R5-Z1W-R2-07 | RPP-R5-A2 | RPP-R5-B2 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R5-W | LL-R5-W |  | CDIST-A-02 | CDIST-L-02 | CC-R5W | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02
RACK-R5-Z1W-R2-08 | RPP-R5-A2 | RPP-R5-B2 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R5-W | LL-R5-W |  | CDIST-A-02 | CDIST-L-02 | CC-R5W | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02
RACK-R5-Z1W-R2-09 | RPP-R5-A2 | RPP-R5-B2 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R5-W | LL-R5-W |  | CDIST-A-02 | CDIST-L-02 | CC-R5W | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02
RACK-R5-Z1W-R2-10 | RPP-R5-A2 | RPP-R5-B2 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R5-W | LL-R5-W |  | CDIST-A-02 | CDIST-L-02 | CC-R5W | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02
RACK-R5-Z1W-R2-11 | RPP-R5-A2 | RPP-R5-B2 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R5-W | LL-R5-W |  | CDIST-A-02 | CDIST-L-02 | CC-R5W | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02
RACK-R5-Z1W-R2-12 | RPP-R5-A2 | RPP-R5-B2 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R5-W | LL-R5-W |  | CDIST-A-02 | CDIST-L-02 | CC-R5W | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02
RACK-R5-Z2E-R1-01 | RPP-R5-A3 | RPP-R5-B3 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R5-E | LL-R5-E |  | CDIST-A-02 | CDIST-L-02 | CC-R5E | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02
RACK-R5-Z2E-R1-02 | RPP-R5-A3 | RPP-R5-B3 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R5-E | LL-R5-E |  | CDIST-A-02 | CDIST-L-02 | CC-R5E | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02
RACK-R5-Z2E-R1-03 | RPP-R5-A3 | RPP-R5-B3 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R5-E | LL-R5-E |  | CDIST-A-02 | CDIST-L-02 | CC-R5E | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02
RACK-R5-Z2E-R1-04 | RPP-R5-A3 | RPP-R5-B3 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R5-E | LL-R5-E |  | CDIST-A-02 | CDIST-L-02 | CC-R5E | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02
RACK-R5-Z2E-R1-05 | RPP-R5-A3 | RPP-R5-B3 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R5-E | LL-R5-E |  | CDIST-A-02 | CDIST-L-02 | CC-R5E | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02
RACK-R5-Z2E-R1-06 | RPP-R5-A3 | RPP-R5-B3 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R5-E | LL-R5-E |  | CDIST-A-02 | CDIST-L-02 | CC-R5E | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02
RACK-R5-Z2E-R1-07 | RPP-R5-A3 | RPP-R5-B3 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R5-E | LL-R5-E |  | CDIST-A-02 | CDIST-L-02 | CC-R5E | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02
RACK-R5-Z2E-R1-08 | RPP-R5-A3 | RPP-R5-B3 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R5-E | LL-R5-E |  | CDIST-A-02 | CDIST-L-02 | CC-R5E | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02
RACK-R5-Z2E-R1-09 | RPP-R5-A3 | RPP-R5-B3 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R5-E | LL-R5-E |  | CDIST-A-02 | CDIST-L-02 | CC-R5E | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02
RACK-R5-Z2E-R1-10 | RPP-R5-A3 | RPP-R5-B3 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R5-E | LL-R5-E |  | CDIST-A-02 | CDIST-L-02 | CC-R5E | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02
RACK-R5-Z2E-R1-11 | RPP-R5-A3 | RPP-R5-B3 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R5-E | LL-R5-E |  | CDIST-A-02 | CDIST-L-02 | CC-R5E | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02
RACK-R5-Z2E-R1-12 | RPP-R5-A3 | RPP-R5-B3 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R5-E | LL-R5-E |  | CDIST-A-02 | CDIST-L-02 | CC-R5E | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02
RACK-R5-Z2E-R2-01 | RPP-R5-A4 | RPP-R5-B4 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R5-E | LL-R5-E |  | CDIST-A-02 | CDIST-L-02 | CC-R5E | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02
RACK-R5-Z2E-R2-02 | RPP-R5-A4 | RPP-R5-B4 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R5-E | LL-R5-E |  | CDIST-A-02 | CDIST-L-02 | CC-R5E | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02
RACK-R5-Z2E-R2-03 | RPP-R5-A4 | RPP-R5-B4 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R5-E | LL-R5-E |  | CDIST-A-02 | CDIST-L-02 | CC-R5E | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02
RACK-R5-Z2E-R2-04 | RPP-R5-A4 | RPP-R5-B4 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R5-E | LL-R5-E |  | CDIST-A-02 | CDIST-L-02 | CC-R5E | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02
RACK-R5-Z2E-R2-05 | RPP-R5-A4 | RPP-R5-B4 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R5-E | LL-R5-E |  | CDIST-A-02 | CDIST-L-02 | CC-R5E | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02
RACK-R5-Z2E-R2-06 | RPP-R5-A4 | RPP-R5-B4 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R5-E | LL-R5-E |  | CDIST-A-02 | CDIST-L-02 | CC-R5E | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02
RACK-R5-Z2E-R2-07 | RPP-R5-A4 | RPP-R5-B4 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R5-E | LL-R5-E |  | CDIST-A-02 | CDIST-L-02 | CC-R5E | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02
RACK-R5-Z2E-R2-08 | RPP-R5-A4 | RPP-R5-B4 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R5-E | LL-R5-E |  | CDIST-A-02 | CDIST-L-02 | CC-R5E | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02
RACK-R5-Z2E-R2-09 | RPP-R5-A4 | RPP-R5-B4 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R5-E | LL-R5-E |  | CDIST-A-02 | CDIST-L-02 | CC-R5E | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02
RACK-R5-Z2E-R2-10 | RPP-R5-A4 | RPP-R5-B4 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R5-E | LL-R5-E |  | CDIST-A-02 | CDIST-L-02 | CC-R5E | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02
RACK-R5-Z2E-R2-11 | RPP-R5-A4 | RPP-R5-B4 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R5-E | LL-R5-E |  | CDIST-A-02 | CDIST-L-02 | CC-R5E | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02
RACK-R5-Z2E-R2-12 | RPP-R5-A4 | RPP-R5-B4 | RPDU-R5-A | RPDU-R5-B | UPS-02-A | UPS-02-B | UTIL-01 | UTIL-02 | AIRZONE-R5-E | LL-R5-E |  | CDIST-A-02 | CDIST-L-02 | CC-R5E | BDL-R5 | BDL-RPDU-R5 | BDL-UPS-02

## UpstreamType
Node Type (as in local table) | Node Type (as in topology) | Upstream Capacity Node Type (as in local table) | Upstream Node Type (as in Topology) | Upstream Contraint Topology | Subdomain Capacity Node Type (as in local table) | Subdomain Node Type (as in Topology) | Subdomain Contraint Topology
Rack | Rack | RPP(A) | RPP | Electrical
Rack | Rack | RPP(B) | RPP | Electrical
Rack | Rack | Room PDU (A) | Room PDU | Electrical
Rack | Rack | Room PDU (B) | Room PDU | Electrical
Rack | Rack | UPS (A) | UPS | Electrical
Rack | Rack | UPS (B) | UPS | Electrical
Rack | Rack | Utility Feed (A) | Utility Feed | Electrical
Rack | Rack | Utility Feed (B) | Utility Feed | Electrical
Rack | Rack | Air Zone | Air Zone | Cooling
Rack | Rack | Liquid Loop | Liquid Loop | Cooling
Rack | Rack | Cooling Distribution (Combined) | Cooling Distribution | Cooling
Rack | Rack | Cooling Distribution (Air) | Cooling Distribution | Cooling
Rack | Rack | Cooling Distribution (Liquid) | Cooling Distribution | Cooling
RPP (A) | RPP | Room PDU (A) | Room PDU | Electrical
RPP (A) | RPP | UPS (A) | UPS | Electrical
RPP (A) | RPP | Utility Feed (A) | Utility Feed | Electrical
RPP (B) | RPP | Room PDU (B) | Room PDU | Electrical
RPP (B) | RPP | UPS (B) | UPS | Electrical
RPP (B) | RPP | Utility Feed (B) | Utility Feed | Electrical
Room PDU (A) | Room PDU | UPS (A) | UPS | Electrical
Room PDU (A) | Room PDU | Utility Feed (A) | Utility Feed | Electrical
Room PDU (B) | Room PDU | UPS (B) | UPS | Electrical
Room PDU (B) | Room PDU | Utility Feed (B) | Utility Feed | Electrical
UPS (A) | UPS | Utility Feed (A) | Utility Feed | Electrical
UPS (B) | UPS | Utility Feed (B) | Utility Feed | Electrical
Air Zone | Air Zone | Cooling Distribution (Combined) | Cooling Distribution | Cooling
Air Zone | Air Zone | Cooling Distribution (Air) | Cooling Distribution | Cooling
Liquid Loop | Liquid Loop | Cooling Distribution (Combined) | Cooling Distribution | Cooling
Liquid Loop | Liquid Loop | Cooling Distribution (Liquid) | Cooling Distribution | Cooling
Capacity Cell | Capacity Cell |  |  |  | RPP(A) | RPP | Electrical
Capacity Cell | Capacity Cell |  |  |  | RPP(B) | RPP | Electrical
Capacity Cell | Capacity Cell |  |  |  | Air Zone | Air Zone | Cooling
Capacity Cell | Capacity Cell |  |  |  | Liquid Loop | Liquid Loop | Cooling
Capacity Cell | Capacity Cell | Room PDU (A) | Room PDU | Electrical
Capacity Cell | Capacity Cell | Room PDU (B) | Room PDU | Electrical
Capacity Cell | Capacity Cell | UPS (A) | UPS | Electrical
Capacity Cell | Capacity Cell | UPS (B) | UPS | Electrical
Capacity Cell | Capacity Cell | Utility Feed (A) | Utility Feed | Electrical
Capacity Cell | Capacity Cell | Utility Feed (B) | Utility Feed | Electrical
Capacity Cell | Capacity Cell | Cooling Distribution (Combined) | Cooling Distribution | Cooling
Capacity Cell | Capacity Cell | Cooling Distribution (Air) | Cooling Distribution | Cooling
Capacity Cell | Capacity Cell | Cooling Distribution (Liquid) | Cooling Distribution | Cooling
Room Bundle | Room Bundle |  |  |  | RPP(A) | RPP | Electrical
Room Bundle | Room Bundle |  |  |  | RPP(B) | RPP | Electrical
Room Bundle | Room Bundle |  |  |  | Air Zone | Air Zone | Cooling
Room Bundle | Room Bundle |  |  |  | Liquid Loop | Liquid Loop | Cooling
Room Bundle | Room Bundle |  |  |  | Room PDU (A) | Room PDU | Electrical
Room Bundle | Room Bundle |  |  |  | Room PDU (B) | Room PDU | Electrical
Room Bundle | Room Bundle | UPS (A) | UPS | Electrical
Room Bundle | Room Bundle | UPS (B) | UPS | Electrical
Room Bundle | Room Bundle | Utility Feed (A) | Utility Feed | Electrical
Room Bundle | Room Bundle | Utility Feed (B) | Utility Feed | Electrical
Room Bundle | Room Bundle | Cooling Distribution (Combined) | Cooling Distribution | Cooling
Room Bundle | Room Bundle | Cooling Distribution (Air) | Cooling Distribution | Cooling
Room Bundle | Room Bundle | Cooling Distribution (Liquid) | Cooling Distribution | Cooling
Room PDU Bundle | Room PDU Bundle |  |  |  | RPP(A) | RPP | Electrical
Room PDU Bundle | Room PDU Bundle |  |  |  | RPP(B) | RPP | Electrical
Room PDU Bundle | Room PDU Bundle |  |  |  | Air Zone | Air Zone | Cooling
Room PDU Bundle | Room PDU Bundle |  |  |  | Liquid Loop | Liquid Loop | Cooling
Room PDU Bundle | Room PDU Bundle |  |  |  | Room PDU (A) | Room PDU | Electrical
Room PDU Bundle | Room PDU Bundle |  |  |  | Room PDU (B) | Room PDU | Electrical
Room PDU Bundle | Room PDU Bundle | UPS (A) | UPS | Electrical
Room PDU Bundle | Room PDU Bundle | UPS (B) | UPS | Electrical
Room PDU Bundle | Room PDU Bundle | Utility Feed (A) | Utility Feed | Electrical
Room PDU Bundle | Room PDU Bundle | Utility Feed (B) | Utility Feed | Electrical
Room PDU Bundle | Room PDU Bundle | Cooling Distribution (Combined) | Cooling Distribution | Cooling
Room PDU Bundle | Room PDU Bundle | Cooling Distribution (Air) | Cooling Distribution | Cooling
Room PDU Bundle | Room PDU Bundle | Cooling Distribution (Liquid) | Cooling Distribution | Cooling
UPS Bundle | UPS Bundle |  |  |  | RPP(A) | RPP | Electrical
UPS Bundle | UPS Bundle |  |  |  | RPP(B) | RPP | Electrical
UPS Bundle | UPS Bundle |  |  |  | Air Zone | Air Zone | Cooling
UPS Bundle | UPS Bundle |  |  |  | Liquid Loop | Liquid Loop | Cooling
UPS Bundle | UPS Bundle |  |  |  | Room PDU (A) | Room PDU | Electrical
UPS Bundle | UPS Bundle |  |  |  | Room PDU (B) | Room PDU | Electrical
UPS Bundle | UPS Bundle |  |  |  | UPS (A) | UPS | Electrical
UPS Bundle | UPS Bundle |  |  |  | UPS (B) | UPS | Electrical
UPS Bundle | UPS Bundle | Utility Feed (A) | Utility Feed | Electrical
UPS Bundle | UPS Bundle | Utility Feed (B) | Utility Feed | Electrical
UPS Bundle | UPS Bundle | Cooling Distribution (Combined) | Cooling Distribution | Cooling
UPS Bundle | UPS Bundle | Cooling Distribution (Air) | Cooling Distribution | Cooling
UPS Bundle | UPS Bundle | Cooling Distribution (Liquid) | Cooling Distribution | Cooling

## Deployment
Deployment | Cluster | Placement Plan | Placement Draft | Capacity Cell
Meridian | SJ-Meridian-C01 | SJ-Meridian-C01-PP01 |  | CC-R1R2
Pacific | SJ-Pacific-C01 |  | SJ-Pacific-C01-PD01 | CC-R3
|  |  | SJ-Pacific-C01-PD02 | CC-R3
|  |  | SJ-Pacific-C01-PD03 | CC-R3
Keystone | SJ-Keystone-C01 | SJ-Keystone-C01-PP01 |  | CC-R5E
Keystone | SJ-Keystrone-C02

## Device Rating Ref
Common RPP Classes
RPP Breaker / Bus Rating | Rated kW (3-phase ~415 V) | 80% Derated kW
225 A | ~162 kW | 130 kW
400 A | ~288 kW | 230 kW
600 A | ~431 kW | 345 kW
800 A | ~575 kW | 460 kW
1200 A (HD RPP) | ~863 kW | 690 kW
1600 A (HD RPP) | ~1,150 kW | 920 kW
2000 A (HD RPP) | ~1,438 kW | 1,150 kW
2400 A (HD RPP) | ~1,725 kW | 1,380 kW
The RPP device capacity is usually intentionally larger than the deployed rack load because:
circuits must remain flexible
loads are uneven across rows
some breaker slots remain unused
So in practice:
RPP device capacity ≈ 1.3–2× the typical rack load it feeds
Room PDU / PDU Transformer Ratings
Transformer Rating | Approx Current (A) | Approx kW
150 kVA | ~210 A | ~120 kW
225 kVA | ~313 A | ~180 kW
300 kVA | ~417 A | ~240 kW
500 kVA | ~695 A | ~400 kW
750 kVA | ~1040 A | ~600 kW
1000 kVA | ~1390 A | ~800 kW
1500 kVA | ~2080 A | ~1200 kW
2000 kVA | ~2780 A | ~1600 kW
UPS System Ratings (system-level)
UPS Rating | Approx Current (A) | Approx kW
250 kW | ~350 A | 250 kW
500 kW | ~700 A | 500 kW
750 kW | ~1040 A | 750 kW
1 MW | ~1390 A | 1000 kW
1.5 MW | ~2080 A | 1500 kW
2 MW | ~2780 A | 2000 kW
3 MW | ~4170 A | 3000 kW
4 MW | ~5560 A | 4000 kW
Common Rack Circuit Breaker
Rack Circuit Capacity (rated) | Approx Current | Apporx kW | derated (raw) | derated (actual)
| 15 | 5.4038 | 4.3231
| 20 | 7.2051 | 5.7641
| 30 | 10.8077 | 8.6461
| 40 | 14.4102 | 11.5282
18 | 50 | 18.0128 | 14.4102 | 15
| 60 | 21.6154 | 17.2923
25 | 70 | 25.2179 | 20.1743 | 20
| 80 | 28.8205 | 23.0564
| 90 | 32.423 | 25.9384
36 | 100 | 36.0256 | 28.8205 | 30
| 125 | 45.032 | 36.0256
54 | 150 | 54.0384 | 43.2307 | 45
| 175 | 63.0448 | 50.4358
72 | 200 | 72.0512 | 57.641 | 60
| 225 | 81.0576 | 64.8461
| 250 | 90.064 | 72.0512
| 300 | 108.0768 | 86.4614
Typical RPP pole capacities
Panel Pole Capacity | Typical Use
42 poles | small distribution panels | 14
54 poles | medium panels | 18
72 poles | larger RPP panels | 24
84 poles | very common in data centers | 28
120 poles | large high-density RPP | 40
A pole corresponds to one phase connection.
A 3-phase rack breaker uses 3 poles.
So an 84-pole RPP can host up to 28 three-phase rack circuits.

## Capacity Name Ref
Node Type | Operational Capacity Name | Device Limit Name (rated) | Device Capacity Name (design) | Operational Capacity Name (Capacity Used for Capacity Margin) | Operating Margin Name | Operating Margin % Name | Device Capacity Name | Device Rating Name
Rack | Rack_Circuit_Capacity_(design) |  |  | Rack_Circuit_Capacity_(design) | Local_Capacity_Margin | Local_Capacity_Margin%
Row | Rack_Circuit_Capacity_(design) |  |  | NA | NA | NA
CDU |  | Rated_Cooling_Capacity |  | NA | NA | NA |  | Rated_Cooling_Capacity
RPP |  | RPP_Panel_Capacity_(rated) | RPP_Panel_Capacity_(design) | RPP_Panel_Capacity_(design) | Device_Capacity_Margin | Device_Capacity_Margin% |  | RPP_Panel_Capacity_(rated)
Air Zone | AirZone_Cooling_Capacity |  |  | AirZone_Cooling_Capacity | Local_Capacity_Margin | Local_Capacity_Margin%
Liquid Loop | LL_Cooling_Capacity |  |  | LL_Cooling_Capacity | Local_Capacity_Margin | Local_Capacity_Margin%
Air Cooling Unit |  | Rated_Cooling_Capacity |  | NA | Local_Capacity_Margin | Local_Capacity_Margin% |  | Rated_Cooling_Capacity
Room PDU | RPDU_Operational_Cap | RPDU_Transformer_Rating | RPDU_Design_Capacity | RPDU_Operational_Cap | Local_Capacity_Margin | Local_Capacity_Margin% | RPDU_Design_Capacity | RPDU_Transformer_Rating
UPS | UPS_Operational_Cap | UPS_Rated_Capacity | UPS_Design_Capacity | UPS_Operational_Cap | Local_Capacity_Margin | Local_Capacity_Margin% | UPS_Design_Capacity | UPS_Rated_Capacity
Capacity Cell | Capacity_Envelope |  |  | Capacity_Envelope | Cell_Margin | Cell_Margin%
Room Bundle | Capacity_Envelope |  |  | Capacity_Envelope | Bundle_Margin | Bundle_Margin%
Room PDU Bundle | Capacity_Envelope |  |  | Capacity_Envelope | Bundle_Margin | Bundle_Margin%
UPS Bundle | Capacity_Envelope |  |  | Capacity_Envelope | Bundle_Margin | Bundle_Margin%
Cooling Distribution | Liquid_Cooling_Capacity |  |  | Liquid_Cooling_Capacity | Local_Capacity_Margin | Local_Capacity_Margin%
Cooling Distribution | Air_Cooling_Capacity |  |  | Air_Cooling_Capacity | Local_Capacity_Margin | Local_Capacity_Margin%