## iDOT
Node Type | DOT Name | iDOT Name | Object Type | Object ID | Object Name (Variable Name) | Object Privacy | Variable Data Type | Unit Class | Default Unit | Validation Rule | Validation List | Extensivity | Formula | Date-Time Format | Max Character | Classifer1 | Classifier1 Values | Classifer2 | Classifier2 Values | Classifer3 | Classifier3 Values
Compute Node | Node Fitness Index | Node Fitness Index
Node_Fitness_Index
Rack | Rack Power Fitness | Rack Power Fitness
Power_Fitness_Index
Power_Headroom_Factor
Power_RampRate_Factor
Power_Burstiness_Factor
Power_PeakRisk_Factor
Power_Overlimit_Factor
Power_Headroom.MIN(30s)
Relative_Power_Headroom.MIN(30s)
Power_RampRate.60s
Power_RampRate.120s
Power_SteepJump_Count.60s
Power_SteepJump_Count.5m
Power_Burstiness.60s
Power_Burstiness.5m
Power_Overshoot.60s
Power_Overshoot.15m
Relative_Power_Overshoot.60s
Relative_Power_Overshoot.15m
Power_Peak_Probability.1m
Power_Peak_Probability.5m
Power_Overlimit_Time.60s
Power_Overlimit_Time.15m
Power_Usage
Norm_Power_IncRate
Power_Overlimit_Event
Rack | Rack Thermal Fitness | Rack Thermal Fitness
Thermal_Fitness_Index
Thermal_Headroom_Factor
Thermal_Hotspot_Factor
Thermal_Overheat_Factor
Thermal_Headroom
Thermal_Headroom.MIN(10m)
Thermal_Headroom.MIN(30m)
Termal_Coupling.10m
Termal_Coupling.30m
Local_Temp_Diff
Local_Temp_Diff.MAX(10m)
Local_Temp_Diff.MAX(30m)
Thermal_Overshoot.5m
Thermal_Overshoot.15m
Thermal_Overheat_Time.5m
Thermal_Overheat_Time.15m
Temperature.Inlet
Termperature.InletTop
Termperature.InletBottom
Thermal_Overheat_Event
Rack | Rack Cooling Efficiency | Rack Cooling Efficiency
Cooling_Efficiency_Index
Thermal_Coupling_Factor
Cooling_Efficiencty_Factor
Server | Server Power Fitness | Server Power Fitness
Power_Fitness_Index
Power_Headroom_Factor
Power_PeakRisk_Factor
Power_Overlimit_Factor
Power_Headroom.MIN(30s)
Relative_Power_Headroom.MIN(30s)
Power_Usage
Power_Overshoot.60s
Power_Overshoot.15m
Relative_Power_Overshoot.60s
Relative_Power_Overshoot.15m
Power_Peak_Probability.1m
Power_Peak_Probability.5m
Power_Overlimit_Time.60s
Power_Overlimit_Time.15m
Power_Overlimit_Event
Server | Server Thermal Fitness | Server Thermal Fitness
Thermal_Fitness_Index
Thermal_Headroom_Factor
Thermal_Overheat_Factor
Fan_Saturation_Factor
Thermal_Headroom
Thermal_Headroom.MIN(10m)
Thermal_Headroom.MIN(30m)
Temperature.Inlet
Fan_Saturation.AVG(30s)
Liquid Loop | Liquid Loop Cooling Finess | Liquid Loop Cooling Finess
LiquidCooling_Fitness_Index
Liquid_SupplyT_Margin_Factor
Liquid_ReturndT_perkW_Factor
Pump_Saturation_Factor
Liquid_SupplyT_Margin.MIN(10m)
Liquid_SupplyT_Margin.MIN(30m)
Liquid_SupplyTemp
Liquid_ReturndT_perkW.10m
Liquid_ReturndT_perkW.30m
Power_Usage
Pump_Saturation.MAX.5m
Rack | Rack Upstream Power Risk | Rack Upstream Power Risk
Upstream_PowerRisk_Index
UpstreamBreaker_Headroom_Factor
Min_Headroom_UpstreamBreaker.30s
Compute Node | Batching Fitness | Batching Fitness
Batching_Fitness_Index
Batchability_PowerProxy_Factor
Power_Usage_Std.2m
Switch Gear | Switch Gear Power Condition | Switch Gear Power Condition
Breaker_Headroom
Breaker_Headroom.MIIN(30s)
PDU/ RPP | PDU/ RPP Power Condition | PDU/ RPP Power Condition
Breaker_Headroom
Breaker_Headroom.MIIN(30s)
Rack PDU | Rack PDU Power Condition | Rack PDU Power Condition
Breaker_Headroom
Breaker_Headroom.MIIN(30s)
Note on F7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Use these names for system and for UI replace _ with space

## TopologySchemes
Topology | Node Type ID | Node Type | Parent Node Type | Child Node Type | Used in Blueprint
Spatial Topology |  | Site |  | IT Facility | T
Spatial Topology |  | IT Facility | Site | Floor, Roof, Generator Yard, Cooling Yard, Transformer Yard | T
Spatial Topology |  | Floor | IT Facility | Room, Electrical Room, Mechanical Room | T
Spatial Topology |  | Electrical Room | Floor |  | T
Spatial Topology |  | Mechanical Room | Floor | Air Cooling Unit | T
Spatial Topology |  | Air Cooling Unit | Mechanical Room |  | T
Spatial Topology |  | Room | Floor | Zone | T
Spatial Topology |  | Zone | Room | RPP, CDU, Aisle, Row | T
Spatial Topology |  | RPP | Zone |  | T
Spatial Topology |  | CDU | Zone |  | T
Spatial Topology |  | Aisle | Zone |  | T
Spatial Topology |  | Row | Zone | Rack | T
Spatial Topology |  | Rack | Row | Server, Networking Device, Storage Device, Rack PDU | T
Spatial Topology |  | Server | Rack |  | F
Spatial Topology |  | Networking Device | Rack |  | F
Spatial Topology |  | Storage Device | Rack |  | F
Spatial Topology |  | Rack PDU | Rack |  | T
Spatial Topology |  | Roof | IT Facility |  | T
Spatial Topology |  | Generator Yard | IT Facility | Generator | T
Spatial Topology |  | Generator | Generator Yard |  | T
Spatial Topology |  | Cooling Yard | IT Facility | Chiller, Cooling Tower Cell | T
Spatial Topology |  | Chiller | Cooling Yard |  | T
Spatial Topology |  | Cooling Tower Cell | Cooling Yard |  | T
Spatial Topology |  | Transformer Yard | IT Facility | Transformer | T
Spatial Topology |  | Transformer | Transformer Yard
AI Infrastructure Fabric |  | Server | AI Infrastructure Fabric | Compute Node | F
AI Infrastructure Fabric |  | Cluster | AI Infrastructure Fabric | Compute Node | F
AI Infrastructure Fabric |  | Fabric Domain | Cluster | Compute Node | F
AI Infrastructure Fabric |  | Project | AI Infrastructure Fabric | Queue, Inference Application | F
AI Infrastructure Fabric |  | Compute Node | Cluster, Server, Fabric Domain | Model Replica, Job Placement | F
AI Infrastructure Fabric |  | Queue | Project | Job | F
AI Infrastructure Fabric |  | Job | Queue | Job Placement | F
AI Infrastructure Fabric |  | Job Placement | Compute Node, Job |  | F
AI Infrastructure Fabric |  | Inference Application | Project | Model | F
AI Infrastructure Fabric |  | Model | Inference Application | Deployment | F
AI Infrastructure Fabric |  | Deployment | Model | Model Replica | F
AI Infrastructure Fabric |  | Model Replica | Compute Node, Model Replica |  | F
Operational Infrastructure |  | IT Facility | Operational Infrastructure | Floor | F
Operational Infrastructure |  | Floor | IT Facility | Room | F
Operational Infrastructure |  | Room | Floor | Zone | F
Operational Infrastructure |  | Zone | Room | Row | F
Operational Infrastructure |  | Row | Zone | Rack, Aisle | F
Operational Infrastructure |  | Aisle | Row |  | F
Operational Infrastructure |  | Rack | Row | Server, Networking Device, Storage Device | F
Operational Infrastructure |  | Server | Rack |  | F
Operational Infrastructure |  | Networking Device | Rack |  | F
Operational Infrastructure |  | Storage Device | Rack |  | F
Operational Infrastructure |  | Business Unit | Operational Infrastructure | Team | F
Operational Infrastructure |  | Team | Business Unit | Project | F
Operational Infrastructure |  | Project | Team |  | F
Electrical System |  | Utility Feed | Electrical System | Switch Gear | T
Electrical System |  | Generator | Electrical System | Switch Gear | T
Electrical System |  | Switch Gear | Utility Feed, Generator | UPS, Mechanical Power Panel, BESS | T
Electrical System |  | BESS | Switch Gear | UPS, Mechanical Power Panel | T
Electrical System |  | UPS | Switch Gear, BESS | Room PDU | T
Electrical System |  | Room PDU | UPS | RPP | T
Electrical System |  | RPP | Room PDU | Rack PDU | T
Electrical System |  | Rack | Electrical System | Rack PDU | T
Electrical System |  | Rack PDU | Rack, RPP | Rack PDU Outlet | T
Electrical System |  | Rack PDU Outlet | Rack PDU | Device PSU | F
Electrical System |  | Device PSU | Rack PDU Outlet | Server, Storage Device, Networking Device | F
Electrical System |  | Server | Device PSU |  | F
Electrical System |  | Networking Device | Device PSU |  | F
Electrical System |  | Storage Device | Device PSU |  | F
Electrical System |  | Mechanical Power Panel | Switch Gear, BESS | Chiller, Cooling Tower Cell, Condenser Water Pump, Condenser Chilled Water Pump, Air Cooling Unit, CDU, Secondary Pump, Lighting | T
Electrical System |  | Chiller | Mechanical Power Panel |  | T
Electrical System |  | Cooling Tower Cell | Mechanical Power Panel |  | T
Electrical System |  | Condenser Water Pump | Mechanical Power Panel |  | T
Electrical System |  | Condenser Chilled Water Pump | Mechanical Power Panel |  | T
Electrical System |  | Air Cooling Unit | Mechanical Power Panel |  | T
Electrical System |  | CDU | Mechanical Power Panel |  | T
Electrical System |  | Secondary Pump | Mechanical Power Panel |  | F
Electrical System |  | Lighting | Mechanical Power Panel |  | F
Cooling System |  | Cooling Plant | Cooling System | Cooling Distribution | T
Cooling System |  | Cooling Distribution | Cooling Plant | Air Cooling Unit, CDU | T
Cooling System |  | Air Cooling Unit | Cooling Distribution | Air Zone | T
Cooling System |  | CDU | Cooling Distribution | Liquid Loop | T
Cooling System |  | Air Zone | Air Cooling Unit | Rack | T
Cooling System |  | Liquid Loop | CDU | Rack | T
Cooling System |  | Rack | Air Zone, Liquid Loop |  | T
Cooling System |  | RDHx | Rack |  | T
Cooling System |  | DTC | Rack |  | T
Cooling System |  | Chiller | Cooling Plant |  | T
Cooling System |  | Cooling Tower Cell | Cooling Plant |  | T
Cooling System |  | Condenser Water Pump | Cooling Plant |  | T
Cooling System |  | Condenser Chilled Water Pump | Cooling Plant |  | T
Asset Inventory |  | Asset Class |  | Asset Type, Vendor | F
Asset Inventory |  | Asset Type | Asset Class | Generator, Transformer, ATS/ STS, UPS, Switch Gear, PDU/ RPP, Rack PDU, Chiller, Cooling Tower Cell, Condenser Water Pump, Condenser Chilled Water Pump, Air Cooling Unit, CDU, Secondary Pump, Rack, Server, Storage Device, Networking Device | F
Asset Inventory |  | Vendor | Asset Class | Generator, Transformer, ATS/ STS, UPS, Switch Gear, PDU/ RPP, Rack PDU, Chiller, Cooling Tower Cell, Condenser Water Pump, Condenser Chilled Water Pump, Air Cooling Unit, CDU, Secondary Pump, Rack, Server, Storage Device, Networking Device | F
Asset Inventory |  | Generator | Asset Type, Vendor |  | F
Asset Inventory |  | Transformer | Asset Type, Vendor |  | F
Asset Inventory |  | ATS/ STS | Asset Type, Vendor |  | F
Asset Inventory |  | BESS | Asset Type, Vendor |  | F
Asset Inventory |  | UPS | Asset Type, Vendor |  | F
Asset Inventory |  | Switch Gear | Asset Type, Vendor |  | F
Asset Inventory |  | PDU/ RPP | Asset Type, Vendor |  | F
Asset Inventory |  | Rack PDU | Asset Type, Vendor |  | F
Asset Inventory |  | Chiller | Asset Type, Vendor |  | F
Asset Inventory |  | Cooling Tower Cell | Asset Type, Vendor |  | F
Asset Inventory |  | Condenser Water Pump | Asset Type, Vendor |  | F
Asset Inventory |  | Condenser Chilled Water Pump | Asset Type, Vendor |  | F
Asset Inventory |  | Air Cooling Unit | Asset Type, Vendor |  | F
Asset Inventory |  | CDU | Asset Type, Vendor |  | F
Asset Inventory |  | Secondary Pump | Asset Type, Vendor |  | F
Asset Inventory |  | Rack | Asset Type, Vendor |  | F
Asset Inventory |  | Server | Asset Type, Vendor |  | F
Asset Inventory |  | Storage Device | Asset Type, Vendor |  | F
Asset Inventory |  | Networking Device | Asset Type, Vendor |  | F
Pod Operations |  | Pod |  | Rack | F
Pod Operations |  | Rack | Pod |  | F
Whitespace Blueprint |  | Site |  | Containment Bundles | T
Whitespace Blueprint |  | Containment Bundles | Site | Room Bundle, Room PDU Bundle, UPS Bundle | T
Whitespace Blueprint |  | Room Bundle | Containment Bundles | Capacity Cell | T
Whitespace Blueprint |  | Room PDU Bundle | Containment Bundles | Capacity Cell | T
Whitespace Blueprint |  | UPS Bundle | Containment Bundles | Capacity Cell | T
Whitespace Blueprint |  | Capacity Cell | Room Bundle, Room PDU Bundle, UPS Bundle | Rack | T
Deploymenbt Blueprint |  | Deployment |  | Cluster | T
Deploymenbt Blueprint |  | Cluster | Deployment | Placement Plan, Placement Draft | T
Deploymenbt Blueprint |  | Placement Plan | Cluster | Capacity Cell, Rack | T
Deploymenbt Blueprint |  | Placement Draft | Cluster | Capacity Cell, Rack | T
Deploymenbt Blueprint |  | Capacity Cell | Placement Plan, Placement Draft |  | T
Deploymenbt Blueprint |  | Rack | Placement Plan, Placement Draft |  | T
Note on E29: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Missing "Fabric Domain"
Note on E32: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Should update here also "Workload" Reply: yes
Note on A41: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: In demo we add new node type "Switch Gear". Shall we also add here for OI topology? Reply: We can use what we have in this file we can ignore switch gear
Note on E57: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Should add BESS here Reply: yes
Note on E85: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Missing "RDHx, DTC" Reply: We shall add them
Note on E94: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Missing "BESS"
Note on E95: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Missing "BESS"
Note on C102: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: This should be "RPP" Reply: RPP
Note on C125: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: should add Rack for Whitespace
Note on A126: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: spelling mistake

## EdgeTypes
Topology | Edge Type ID | Parent Node Type | Child Node Type | Min_Link | Max_Link | Edge Property
Spatial Topology |  | Site | IT Facility | 1 | 25
Spatial Topology |  | IT Facility | Floor | 1 | 25
Spatial Topology |  | Floor | Room | 1 | 25
Spatial Topology |  | Room | Zone | 1 | 25
Spatial Topology |  | Zone | Row | 1 | 25
Spatial Topology |  | Row | Rack | 1 | 100
Spatial Topology |  | Rack | Rack PDU | 1 | 10
Spatial Topology |  | Rack | Server | 1 | 50
Spatial Topology |  | Rack | Networking Device | 0 | 50
Spatial Topology |  | Rack | Storage Device | 0 | 50
Spatial Topology |  | Zone | Aisle | 1 | 50
Spatial Topology |  | Zone | RPP | 0 | 25
Spatial Topology |  | Zone | CDU | 0 | 25
Spatial Topology |  | Floor | Electrical Room | 0 | 10
Spatial Topology |  | Floor | Mechanical Room | 0 | 10
Spatial Topology |  | Mechanical Room | Air Cooling Unit | 0 | 100
Spatial Topology |  | IT Facility | Roof | 0 | 10
Spatial Topology |  | IT Facility | Generator Yard | 0 | 10
Spatial Topology |  | Generator Yard | Generator | 0 | 25
Spatial Topology |  | IT Facility | Cooling Yard | 0 | 10
Spatial Topology |  | Cooling Yard | Chiller | 0 | 25
Spatial Topology |  | Cooling Yard | Cooling Tower Cell | 0 | 25
Spatial Topology |  | IT Facility | Transformer Yard | 0 | 10
Spatial Topology |  | Transformer Yard | Transformer | 0 | 25
AI Infrastructure Fabric |  | Cluster | Compute Node | 0 | 50000
AI Infrastructure Fabric |  | Cluster | Fabric Domain | 0 | 100
AI Infrastructure Fabric |  | Fabric Domain | Compute Node | 0 | 5000
AI Infrastructure Fabric |  | Server | Compute Node | 0 | 10
AI Infrastructure Fabric |  | Compute Node | Model Replica | 0 | 10
AI Infrastructure Fabric |  | Compute Node | Job Placement | 0 | 50
AI Infrastructure Fabric |  | Project | Queue | 0 | 100
AI Infrastructure Fabric |  | Queue | Job | 0 | 100
AI Infrastructure Fabric |  | Job | Job Placement | 0 | 100
AI Infrastructure Fabric |  | Project | Inference Application | 0 | 100
AI Infrastructure Fabric |  | Inference Application | Model | 0 | 100
AI Infrastructure Fabric |  | Model | Deployment | 0 | 100
AI Infrastructure Fabric |  | Deployment | Model Replica | 0 | 500
Operational Infrastructure |  | IT Facility | Floor | 1 | 25
Operational Infrastructure |  | Floor | Room | 1 | 25
Operational Infrastructure |  | Room | Zone | 1 | 25
Operational Infrastructure |  | Zone | Row | 1 | 25
Operational Infrastructure |  | Row | Rack | 1 | 100
Operational Infrastructure |  | Rack | Networking Device | 0 | 50
Operational Infrastructure |  | Rack | Storage Device | 0 | 50
Operational Infrastructure |  | Rack | Server | 0 | 50
Operational Infrastructure |  | Row | Aisle | 1 | 10
Operational Infrastructure |  | Business Unit | Team | 0 | 100
Operational Infrastructure |  | Team | Project | 0 | 100
Electrical System |  | Utility Feed | Switch Gear | 1 | 10
Electrical System |  | Generator | Switch Gear | 1 | 10
Electrical System |  | Switch Gear | UPS | 1 | 10
Electrical System |  | Switch Gear | Mechanical Power Panel | 1 | 10
Electrical System |  | Switch Gear | BESS | 0 | 10
Electrical System |  | BESS | UPS | 1 | 10
Electrical System |  | BESS | Mechanical Power Panel | 1 | 10
Electrical System |  | UPS | Room PDU | 1 | 100
Electrical System |  | Room PDU | RPP | 1 | 100
Electrical System |  | RPP | Rack PDU | 1 | 100
Electrical System |  | Rack | Rack PDU | 1 | 10
Electrical System |  | Rack PDU | Rack PDU Outlet | 1 | 100
Electrical System |  | Rack PDU Outlet | Device PSU | 1 | 10
Electrical System |  | Device PSU | Server | 1 | 10
Electrical System |  | Device PSU | Storage Device | 1 | 10
Electrical System |  | Device PSU | Networking Device | 1 | 10
Electrical System |  | Mechanical Power Panel | Chiller | 0 | 50
Electrical System |  | Mechanical Power Panel | Cooling Tower Cell | 0 | 50
Electrical System |  | Mechanical Power Panel | Condenser Water Pump | 0 | 100
Electrical System |  | Mechanical Power Panel | Condenser Chilled Water Pump | 0 | 100
Electrical System |  | Mechanical Power Panel | Air Cooling Unit | 0 | 100
Electrical System |  | Mechanical Power Panel | CDU | 0 | 100
Electrical System |  | Mechanical Power Panel | Secondary Pump | 0 | 100
Electrical System |  | Mechanical Power Panel | Lighting | 0 | 100
Cooling System |  | Cooling Plant | Cooling Distribution | 0 | 10
Cooling System |  | Cooling Distribution | Air Cooling Unit | 0 | 100
Cooling System |  | Cooling Distribution | CDU | 0 | 100
Cooling System |  | Air Cooling Unit | Air Zone | 1 | 10
Cooling System |  | CDU | Liquid Loop | 1 | 10
Cooling System |  | Air Zone | Rack | 1 | 100
Cooling System |  | Liquid Loop | Rack | 1 | 100
Cooling System |  | Rack | RDHx | 0 | 10
Cooling System |  | Rack | DTC | 0 | 10
Cooling System |  | Cooling Plant | Chiller | 0 | 50
Cooling System |  | Cooling Plant | Cooling Tower Cell | 0 | 50
Cooling System |  | Cooling Plant | Condenser Water Pump | 0 | 100
Cooling System |  | Cooling Plant | Condenser Chilled Water Pump | 0 | 100
Asset Inventory |  | Asset Class | Asset Type | 1 | 100
Asset Inventory |  | Asset Class | Vendor | 1 | 250
Asset Inventory |  | Asset Type | Generator | 0 | 1000
Asset Inventory |  | Asset Type | Transformer | 0 | 1000
Asset Inventory |  | Asset Type | ATS/ STS | 0 | 1000
Asset Inventory |  | Asset Type | BESS | 0 | 1000
Asset Inventory |  | Asset Type | UPS | 0 | 1000
Asset Inventory |  | Asset Type | Switch Gear | 0 | 1000
Asset Inventory |  | Asset Type | Room PDU | 0 | 2500
Asset Inventory |  | Asset Type | RPP | 0 | 2500
Asset Inventory |  | Asset Type | Rack PDU | 0 | 10000
Asset Inventory |  | Asset Type | Chiller | 0 | 1000
Asset Inventory |  | Asset Type | Cooling Tower Cell | 0 | 1000
Asset Inventory |  | Asset Type | Condenser Water Pump | 0 | 10000
Asset Inventory |  | Asset Type | Condenser Chilled Water Pump | 0 | 10000
Asset Inventory |  | Asset Type | Air Cooling Unit | 0 | 1000
Asset Inventory |  | Asset Type | CDU | 0 | 10000
Asset Inventory |  | Asset Type | Secondary Pump | 0 | 10000
Asset Inventory |  | Asset Type | Rack PDU | 0 | 10000
Asset Inventory |  | Asset Type | Server | 0 | 100000
Asset Inventory |  | Asset Type | Storage Device | 0 | 100000
Asset Inventory |  | Asset Type | Networking Device | 0 | 100000
Asset Inventory |  | Vendor | Generator | 0 | 1000
Asset Inventory |  | Vendor | Transformer | 0 | 1000
Asset Inventory |  | Vendor | ATS/ STS | 0 | 1000
Asset Inventory |  | Vendor | BESS | 0 | 1000
Asset Inventory |  | Vendor | UPS | 0 | 1000
Asset Inventory |  | Vendor | Switch Gear | 0 | 1000
Asset Inventory |  | Vendor | Room PDU | 0 | 2500
Asset Inventory |  | Vendor | RPP | 0 | 2500
Asset Inventory |  | Vendor | Rack PDU | 0 | 10000
Asset Inventory |  | Vendor | Chiller | 0 | 1000
Asset Inventory |  | Vendor | Cooling Tower Cell | 0 | 1000
Asset Inventory |  | Vendor | Condenser Water Pump | 0 | 10000
Asset Inventory |  | Vendor | Condenser Chilled Water Pump | 0 | 10000
Asset Inventory |  | Vendor | Air Cooling Unit | 0 | 1000
Asset Inventory |  | Vendor | CDU | 0 | 10000
Asset Inventory |  | Vendor | Secondary Pump | 0 | 10000
Asset Inventory |  | Vendor | Rack PDU | 0 | 10000
Asset Inventory |  | Vendor | Server | 0 | 100000
Asset Inventory |  | Vendor | Storage Device | 0 | 100000
Asset Inventory |  | Vendor | Networking Device | 0 | 100000
Pod Operations |  | Pod | Rack | 1 | 10000
Whitespace Blueprint |  | Site | Containment Bundles | 1 | 100
Whitespace Blueprint |  | Containment Bundles | Room Bundle | 0 | 100
Whitespace Blueprint |  | Containment Bundles | Room PDU Bundle | 0 | 100
Whitespace Blueprint |  | Containment Bundles | UPS Bundle | 0 | 100
Whitespace Blueprint |  | Room Bundle | Capacity Cell | 1 | 100
Whitespace Blueprint |  | Room PDU Bundle | Capacity Cell | 1 | 100
Whitespace Blueprint |  | UPS Bundle | Capacity Cell | 1 | 100
Whitespace Blueprint |  | Capacity Cell | Rack | 0 | 10000
Deployment Blueprint |  | Deployment | Cluster | 1 | 100
Deployment Blueprint |  | Cluster | Placement Plan | 0 | 1
Deployment Blueprint |  | Cluster | Placement Draft | 0 | 25
Deployment Blueprint |  | Placement Plan | Capacity Cell | 0 | 100
Deployment Blueprint |  | Placement Plan | Rack | 0 | 10000
Deployment Blueprint |  | Placement Draft | Capacity Cell | 0 | 100
Deployment Blueprint |  | Placement Draft | Rack | 0 | 10000
Note on D43: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Zone (Aisle) is renamed as "Row"

## iSET
Node Type | SET Name | iSET Name | Field Type | Field ID | Field Name | Field Privacy | Variable Data Type | Unit Class | Default Unit | Validation Rule | Validation List | Show As Multiple Choice | Multiple Choice Limit | Formula | Date-Time Format | Max Character | Average Character | Classifer1 | Classifier1 Field IDs | Classifier1 Values | Classifer2 | Classifier2 Field IDs | Classifier2 Values | Classifer3 | Classifier3 Field IDs | Classifier3 Values
Rack | Rack Operating Constraints | Rack Operating Constraints
[5 empty] | Rated_Power_Capacity |  | PIT(2)
[5 empty] | Breaker_PowerLimit.Inherited |  | PIT(2)
[5 empty] | Power_Derating_Factor |  | PIT(2)
[5 empty] | Effective_Power_Limit |  | PIT(2)
[5 empty] | Thermal_Limit |  | PIT(2)
Server | Server Operating Constraints | Server Operating Constraints
[5 empty] | Power_Derating_Factor |  | PIT(2)
[5 empty] | Effective_Power_Limit |  | PIT(2)
[5 empty] | Thermal_Limit |  | PIT(2)
[5 empty] | Fan_Speed_Limit |  | PIT(2)
Liquid Loop | Liquid Loop Operating Constraints | Liquid Loop Operating Constraints
[5 empty] | Liquid_SupplyT_Limit |  | PIT(2)
[5 empty] | Pump_Speed_Limit |  | PIT(2)
Switch Gear | Switch Gear Operating Constraints | Switch Gear Operating Constraints
[5 empty] | Breaker_CurrentLimit |  | PIT(2)
[5 empty] | Breaker_PowerLimit |  | PIT(2)
[5 empty] | Power_Derating_Factor |  | PIT(2)
[5 empty] | Effective_Power_Limit |  | PIT(2)
PDU/ RPP | PDU/ RPP Operating Constraints | PDU/ RPP Operating Constraints
[5 empty] | Breaker_CurrentLimit |  | PIT(2)
[5 empty] | Breaker_PowerLimit |  | PIT(2)
[5 empty] | Power_Derating_Factor |  | PIT(2)
[5 empty] | Effective_Power_Limit |  | PIT(2)
Rack PDU | Rack PDU Operating Constraints | Rack PDU Operating Constraints
[5 empty] | Breaker_CurrentLimit |  | PIT(2)
[5 empty] | Breaker_PowerLimit |  | PIT(2)
[5 empty] | Power_Derating_Factor |  | PIT(2)
[5 empty] | Effective_Power_Limit |  | PIT(2)
Rack | Rack NFI Metric Weights | Rack NFI Metric Weights
[5 empty] | Power_Headroom_wt |  | PIT(2)
[5 empty] | Power_RampRate_wt |  | PIT(2)
[5 empty] | Power_Burstiness_wt |  | PIT(2)
[5 empty] | Power_PeakRisk_wt |  | PIT(2)
[5 empty] | Power_Overlimit_wt |  | PIT(2)
[5 empty] | Thermal_Headroom_wt |  | PIT(2)
[5 empty] | Thermal_Hotspot_wt |  | PIT(2)
[5 empty] | Thermal_Overheat_wt |  | PIT(2)
[5 empty] | Thermal_Coupling_wt |  | PIT(2)
[5 empty] | Cooling_Efficiencty_wt |  | PIT(2)
[5 empty] | UpstreamBreaker_Headroom_wt |  | PIT(2)
Server | Server NFI Metric Weights | Server NFI Metric Weights
[5 empty] | Power_Headroom_wt |  | PIT(2)
[5 empty] | Power_PeakRisk_wt |  | PIT(2)
[5 empty] | Power_Overlimit_wt |  | PIT(2)
[5 empty] | Thermal_Headroom_wt |  | PIT(2)
[5 empty] | Thermal_Overheat_wt |  | PIT(2)
[5 empty] | Fan_Saturation_wt |  | PIT(2)
Liquid Loop | Liquid Loop NFI Metric Weights | Liquid Loop NFI Metric Weights
[5 empty] | Liquid_SupplyT_Margin_wt |  | PIT(2)
[5 empty] | Liquid_ReturndT_perkW_wt |  | PIT(2)
[5 empty] | Pump_Saturation_wt |  | PIT(2)
Compute Node | Compute Node NFI Metric Weights | Compute Node NFI Metric Weights
[5 empty] | Batchability_PowerProxy_wt |  | PIT(2)
Rack |  | Operational Capacity
Rack_Circuit_Capacity_(rated)
Rack_Circuit_Capacity_(design)
Rack |  | Load Allocation
Allocated_ITLoad
TheorMax_ITLoad
Allocated_AirCool_Load
Allocated_LiquidCool_Load
Rack |  | Other Design Parameters
Rack_AirCool_Fraction
Rack_LiquidCool_Fraction
Rack |  | Capacity Margin
Local_Capacity_Margin
Local_Capacity_Margin%
Rack |  | Upstream Capacity Margin
Upstream_Capacity
Upstream_Load
[5 empty] | Upstream_Capacity_Margin | [12 empty] | Upstream Infrastructure | [Upstream Node Name]
[5 empty] | Upstream_Capacity_Margin% | [12 empty] | Upstream Infrastructure | [Upstream Node Name]
Row |  | Operational Capacity
Rack_Circuit_Capacity_(design)
Rack_Positions
Row |  | Load Allocatioon
Rack_Count
Allocated_ITLoad
CDU |  | Device Capacity
Rated_Cooling_Capacity
Pump_Capacity
RPP |  | Operational Capacity
RPP_Panel_Capacity_(rated)
RPP_Panel_Capacity_(design)
RPP_BreakerPole_Capacity
Rack_Positions
RPP |  | Load Allocation
Rack_Count
Allocated_ITLoad
TheorMax_ITLoad
RPP |  | Capacity Margin
Device_Capacity_Margin
Device_Capacity_Margin%
RPP |  | Upstream Capacity Margin
Upstream_Capacity
Upstream_Load
Upstream_Capacity_Margin
Upstream_Capacity_Margin%
Air Zone |  | Operational Capacity
AirZone_Cooling_Capacity
Maximum_Air_Flow
Rack_Positions
Air Zone |  | Load Allocation
Rack_Count
Allocated_AirCool_Load
TheorMax_AirCool_Load
Air Zone |  | Capacity Margin
Local_Capacity_Margin
Local_Capacity_Margin%
Air Zone |  | Upstream Capacity Margin
[5 empty] | Upstream_Capacity_Margin | [12 empty] | Upstream Infrastructure | [Upstream Node Name]
[5 empty] | Upstream_Capacity_Margin% | [12 empty] | Upstream Infrastructure | [Upstream Node Name]
Air Zone |  | Other Design Parameters
Rack_Inlet_Setpoint
ColdAisle_Supply_Temp
Rack_DeltaT_(design)
Liquid Loop |  | Operational Capacity
LL_Cooling_Capacity
Maximum_Flow_Rate
Rack_Positions
Liquid Loop |  | Load Allocation
Rack_Count
Allocated_LiquidCool_Load
TheorMax_LiquidCool_Load
Liquid Loop |  | Capacity Margin
Local_Capacity_Margin
Local_Capacity_Margin%
Liquid Loop |  | Upstream Capacity Margin
Upstream_Capacity_Margin
Upstream_Capacity_Margin%
Liquid Loop |  | Other Design Parameters
Loop_Supply_Setpoint
Loop_DeltaT_(design)
Air Cooling Unit |  | Device Capacity
Rated_Cooling_Capacity
Maximum_Air_Flow
Room PDU |  | Operational Capacity
RPDU_Transformer_Rating
RPDU_Design_Capacity
RPDU_Operational_Cap
Rack_Positions
Room PDU |  | Load Allocation
Rack_Count
Allocated_ITLoad
TheorMax_ITLoad
Room PDU |  | Capacity Margin
Local_Capacity_Margin
Local_Capacity_Margin%
Device_Capacity_Margin
Device_Capacity_Margin%
Room PDU |  | Upstream Capacity Margin
Upstream_Capacity_Margin
Upstream_Capacity_Margin%
UPS |  | Operational Capacity
UPS_Rated_Capacity
UPS_Design_Capacity
UPS_Operational_Cap
Rack_Positions
UPS |  | Load Allocation
Rack_Count
Allocated_ITLoad
TheorMax_ITLoad
UPS |  | Capacity Margin
Local_Capacity_Margin
Local_Capacity_Margin%
Device_Capacity_Margin
Device_Capacity_Margin%
UPS |  | Upstream Capacity Margin
Upstream_Capacity_Margin
Upstream_Capacity_Margin%
RDHx |  | Operational Capacity
RDHx_MaxHeat_Removal
DTC |  | Operational Capacity
DTC_MaxCool_Capacity
Capacity Cell |  | Operational Capacity
Capacity_Envelope
Power_Capacity
Thermal_Capacity
Rack_Positions
Capacity Cell |  | Load Allocation
Rack_Count
Allocated_ITLoad
TheorMax_ITLoad
Capacity Cell |  | Capacity Margin
Cell_Margin
Cell_Margin%
Cell_Utilization%
Power_Capacity
Power_Margin
Power_Margin%
Thermal_Capacity
Thermal_Margin
Thermal_Margin%
Capacity Cell |  | Subdomain Margin
[5 empty] | Power_Margin | [12 empty] | Electrical infrastructure | [node name]
[5 empty] | Power_Margin% | [12 empty] | Electrical infrastructure | [node name]
[5 empty] | Thermal_Margin | [12 empty] | Cooling infrastructure | [node name]
[5 empty] | Thermal_Margin% | [12 empty] | Cooling infrastructure | [node name]
Capacity Cell |  | Upstream Capacity Margin
[5 empty] | Power_Margin | [12 empty] | Electrical infrastructure | [node name]
[5 empty] | Power_Margin% | [12 empty] | Electrical infrastructure | [node name]
[5 empty] | Thermal_Margin | [12 empty] | Cooling infrastructure | [node name]
[5 empty] | Thermal_Margin% | [12 empty] | Cooling infrastructure | [node name]
Room Bundle |  | Operational Capacity
Capacity_Envelope
Power_Capacity
Thermal_Capacity
Rack_Positions
Room Bundle |  | Load Allocation
Rack_Count
Allocated_ITLoad
TheorMax_ITLoad
Room Bundle |  | Capacity Margin
Bundle_Margin
Bundle_Margin%
Bundle_Utilization%
Power_Margin
Power_Margin%
Thermal_Margin
Thermal_Margin%
Room Bundle |  | Subdomain Margin
[5 empty] | Cell_Margin | [12 empty] | Capacity Cell | [node name]
[5 empty] | Cell_Margin% | [12 empty] | Capacity Cell | [node name]
Power_Margin
Power_Margin%
Thermal_Margin
Thermal_Margin%
Room Bundle |  | Upstream Capacity Margin
Power_Margin
Power_Margin%
Thermal_Margin
Thermal_Margin%
Room PDU Bundle |  | Operational Capacity
Capacity_Envelope
Power_Capacity
Thermal_Capacity
Rack_Positions
Room PDU Bundle |  | Load Allocation
Rack_Count
Allocated_ITLoad
TheorMax_ITLoad
Room PDU Bundle |  | Capacity Margin
Bundle_Margin
Bundle_Margin%
Bundle_Utilization%
Power_Margin
Power_Margin%
Thermal_Margin
Thermal_Margin%
Room PDU Bundle |  | Subdomain Margin
Cell_Margin
Cell_Margin%
Power_Margin
Power_Margin%
Thermal_Margin
Thermal_Margin%
Room PDU Bundle |  | Upstream Capacity Margin
Power_Margin
Power_Margin%
Thermal_Margin
Thermal_Margin%
UPS Bundle |  | Operational Capacity
Capacity_Envelope
Power_Capacity
Thermal_Capacity
Rack_Positions
UPS Bundle |  | Load Allocation
Rack_Count
Allocated_ITLoad
TheorMax_ITLoad
UPS Bundle |  | Capacity Margin
Bundle_Margin
Bundle_Margin%
Bundle_Utilization%
Power_Margin
Power_Margin%
Thermal_Margin
Thermal_Margin%
UPS Bundle |  | Subdomain Margin
Cell_Margin
Cell_Margin%
Power_Margin
Power_Margin%
Thermal_Margin
Thermal_Margin%
UPS Bundle |  | Upstream Capacity Margin
Power_Margin
Power_Margin%
Thermal_Margin
Thermal_Margin%
Cooling Distribution |  | Operational Capacity
Liquid_Cooling_Capacity
Air_Cooling_Capacity
Rack_Positions
Cooling Distribution |  | Load Allocation
Rack_Count
Allocated_AirCool_Load
TheorMax_AirCool_Load
Allocated_LiquidCool_Load
TheorMax_LiquidCool_Load
Cooling Distribution |  | Capacity Margin
Local_Capacity_Margin
Local_Capacity_Margin%

## Variables (updated)
VariableType | Variable Class | Functional Domain | abbreviation | Variables: (VariableType.Modifier) | Description | Node Types | Data Format | Object Type | Unit Class | Variable Data Type | Extensivity | Data Topology | DOT/ SET | RFQ | RIT | SIT | C-SIT | Spatial | Operational Infrastructure | Cooling System | Electrical System | AI Infrastructure Fabric | Pod Operations | Whitespace | Deployment |  | Server | Storage Device | Networking Device | Rack | Row | Aisle | Zone | Room | Floor | Electrical Room | Mechanical Room | Cooling Yard | Generator Yard | Transformer Yard | Roof | IT Facility | Site | Device PSU | Rack PDU Outlet | Rack PDU | RPP | Room PDU | UPS | BESS | Switch Gear | Generator | Transformer | Utility Feed | Lighting | Mechanical Power Panel | RDHx | DTC | Liquid Loop | Air Zone | CDU | Air Cooling Unit | Cooling Distribution | Cooling Plant | Chiller | Condenser Chilled Water Pump | Condenser Water Pump | Cooling Tower Cell | Capacity Cell | Room Bundle | Room PDU Bundle | UPS Bundle | Containment Bundles | Deployment | Cluster | Placement Plan | Placement Draft | Fabric Domain | Inference Application | Compute Node | Job | Job Placement | Model | Model Replica | Queue | Project | Asset Class | Asset Type | ATS/ STS | Secondary Pump | Pod | Business Unit | Team | Vendor | Networking Device | Rack | Server | Storage Device | Business Unit | Floor | IT Facility | Project | Room | Team | Zone | Row | Aisle | Air Cooling Unit | CDU | Chiller | Condenser Chilled Water Pump | Condenser Water Pump | Cooling Tower Cell | Air Zone | Cooling Distribution | Cooling Plant | DTC | Liquid Loop | RDHx | BESS | Device PSU | Generator | Lighting | Mechanical Power Panel | Room PDU | RPP | Rack PDU | Rack PDU Outlet | Secondary Pump | Switch Gear | UPS | Utility Feed | Cluster | Compute Node | Deployment | Fabric Domain | Inference Application | Job | Job Placement | Model | Model Replica | Queue | Pod | Containment Bundles | Room Bundle | Room PDU Bundle | UPS Bundle | Capacity Cell | Deployment | Cluster | Placement Plan | Placement Draft
Power_Usage | Input | Power | pwr_use | Power_Usage |  | Rack, Server, Loop, Compute Node | Number | Variable Number | Power | PIT(2) | Extensive | Integrated | DOT |  |  |  | 5s | Y | Y |  | Y | Y | Y |  |  | Power usage exists at power consumption nodes; It also exists at group entities such as zone and room, which can be seen as a group of power consumers. | Y | Y | Y | Y | Y |  | Y | Y | Y | [6 empty] | Y | Y | [11 empty] | Y | [71 empty] | T | T
Power_Flow | Input | Power |  | Power_Flow |  |  | Number | Variable Number | Power | PIT(2) | Extensive | Integrated | DOT |  |  |  | 5s |  |  |  | Y |  |  |  |  | Power flow exists on the electrical infrastructure nodes | [19 empty] | Y | Y | Y | Y | Y | Y | Y | Y | Y |  | Y
Power_Input | Input | Power |  | Power_Input |  |  | Number | Variable Number | Power | PIT(2) | Extensive | Standalone | DOT | [106 empty] | Y |  |  |  | Y | Y | Y |  |  |  |  | Y
Power_Output | Input | Power |  | Power_Output |  |  | Number | Variable Number | Power | PIT(2) | Extensive | Standalone | DOT | [106 empty] | Y |  |  |  | Y | Y | Y |  |  |  |  | Y | Y
Power_Usage | Input | Power | pwr_use | Power_Usage.gpu(n) | The gpu power consumption are folded as variables into compute nodes | Compute Node | Number | Variable Number | Power | PIT(2) | Extensive | Standalone | DOT | [120 empty] | Y
Rated_Power_Capacity | Reference | Power | pwr_cap_rated | Rated_Power_Capacity | The maximum continuous power a component or system is designed and certified to handle under specified conditions | Rack | Number | Variable Number | Power | PIT(2) | Intensive | Standalone | SET | [81 empty] | Y | Y | Y | Y | [21 empty] | Y | Y | Y |  | Y | Y | Y | Y |  |  | Y | Y
Power_Limit | Reference | Power | pwr_lim | Power_Limit | An enforced ceiling on power usage or delivery, set by controls, policies, or protection mechanisms. This is often set AFTER a derating factor has been applied | Rack PDU, Server PSU | Number | Variable Number | Power | PIT(2) | Intensive | Standalone | SET | [12 empty] | Temporarily cover power limit for nodes that don't. have their specific Power Limit names | [68 empty] | Y | Y | Y | Y |  |  | Y |  | Y |  | Y | [14 empty] | Y | Y | Y |  | Y | Y | Y | Y |  |  | Y | Y |  | Y | Y |  | Y | [6 empty] | Y
Breaker_CurrentLimit | Reference | Power | brk_curlim | Breaker_CurrentLimit | The maximum allowable current (Amps) that a breaker is permitted to carry or interrupt, as enforced by its thermal and magnetic trip mechanisms | Switchgear, PDU/ RPP, Rack PDU | Number | Variable Number | Electrocal Current | PIT(2) | Intensive | Standalone | SET | [17 empty] | 0 | 0 | 0 | 0 | 0 | [84 empty] | Y |  | Y |  | Y | Y | Y | Y |  |  | Y | Y
Breaker_PowerLimit | Reference | Power | brk_pwrlim | Breaker_PowerLimit | The maximum electrical power (Watts or kW) that may pass through the breaker, derived from the current limit and operating voltage. Breaker_PowerLimit=Breaker_CurrentLimit×Nominal_Voltage×Power_Factor | Switchgear, PDU/ RPP, Rack PDU | Number | Variable Number | Power | PIT(2) | Intensive | Standalone | SET | [17 empty] | 0 | 0 | 0 | 0 | 0 | [84 empty] | Y |  | Y |  | Y | Y | Y | Y |  |  | Y | Y
Breaker_PowerLimit | Reference | Power | brk_pwrlim | Breaker_PowerLimit.Inherited | A power limit imposed from an upstream element (panel, PDU, feeder, UPS, or facility policy) that constrains the breaker regardless of its own physical rating. | Rack | Number | Variable Number | Power | PIT(2) | Intensive | Standalone | SET | [81 empty] | Y | Y | Y | Y |  | Y | Y |  | Y |  | Y |  |  | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y |  | Y | Y | Y | Y | Y | Y | Y | Y | Y |  | Y | Y |  | Y | [6 empty] | Y
Power_Derating_Factor | Reference | Power | pwr_derate_fac | Power_Derating_Factor | A dimensionless multiplier (0–1) applied to rated electrical capacity to account for non-reference operating conditions and reliability requirements. | Rack, Server, Switchgear, PDU/ RPP, Rack PDU | Number | Variable Number | Ratio | PIT(2) | Intensive | Standalone | SET | [106 empty] | Y |  | Y |  | Y | Y | Y | Y |  |  | Y | Y
Effective_Power_Limit | Reference | Power | pwr_lim_eff | Effective_Power_Limit | The final enforceable power ceiling after accounting for all applicable constraints, including breaker physics, inherited limits, and derating. | Rack, Server, Switchgear, PDU/ RPP, Rack PDU | Number | Variable Number | Power | PIT(2) | Intensive | Standalone | SET | [12 empty] | Temporarily cover effective power limit for nodes that don't. have their specific Power Limit names | [68 empty] | Y | Y | Y | Y |  | Y | Y |  | Y |  | Y | [14 empty] | Y | Y | Y |  | Y | Y | Y | Y |  |  | Y | Y | Y | Y | Y |  | Y | [6 empty] | Y
Power_Headroom | Metric | Power | pwr_hdr | Power_Headroom |  | Rack, Server | Number | Variable Number | Power | PIT(2) | Intensive | Standalone | DOT | [82 empty] | Y | Y |  |  | Y | Y |  | Y |  | Y | [19 empty] | Y | Y |  |  |  |  | Y
Power_Headroom | Metric | Power | pwr_hdr | Power_Headroom.MIN(30s) | Used for racks and serversa, affecting job placement decisions | Rack, Server | Number | Variable Number | Power | PIT(2) | Intensive | Standalone | DOT | 5s | 30s | [80 empty] | Y | Y
Power_Headroom | Metric | Power |  | Power_Headroom.MIN(120s) | used for zones and PDUs, could affect job placement decisions if close to limit |  | Number | Variable Number | Power | PIT(2) | Intensive | Standalone | DOT | 60s | 120s | [89 empty] | Y | [19 empty] | Y | Y
Power_Headroom | Metric | Power |  | Power_Headroom.MIN(5m) | for UPS. useful to watching if operating near limit |  | Number | Variable Number | Power | PIT(2) | Intensive | Standalone | DOT | 60s | 5m | [115 empty] | Y
Power_Headroom | Metric | Power |  | Power_Headroom.AVG(5m) | For reporting purposes at room, floor, facility levels |  | Number | Variable Number | Power | PIT(2) | Intensive | Standalone | DOT | 5m | 5m | [84 empty] | Y | Y |  | Y
Power_Headroom | Metric | Power |  | Power_Headroom.P95(5m) | For reporting purposes at room, floor, facility levels |  | Number | Variable Number | Power | PIT(2) | Intensive | Standalone | DOT | 5m | 5m | [84 empty] | Y | Y |  | Y
Relative_Power_Headroom | Metric | Power | pwr_hdr_rel | Relative_Power_Headroom |  | Rack, Server | Number | Variable Number | Ratio | PIT(2) | Intensive | Standalone | DOT
Relative_Power_Headroom | Metric | Power | pwr_hdr_rel | Relative_Power_Headroom.MIN(30s) | Used for racks and servers, affecting job placement decisions | Rack, Server | Number | Variable Number | Ratio | PIT(2) | Intensive | Standalone | DOT | 5s | 30s | [80 empty] | Y | Y
Relative_Power_Headroom | Metric | Power |  | Relative_Power_Headroom.MIN(120s) | used for zones and PDUs, could affect job placement decisions if close to limit |  | Number | Variable Number | Ratio | PIT(2) | Intensive | Standalone | DOT | 60s | 120s | [109 empty] | Y | Y
Relative_Power_Headroom | Metric | Power |  | Relative_Power_Headroom.MIN(5m) | for UPS. useful to watching if operating near limit |  | Number | Variable Number | Ratio | PIT(2) | Intensive | Standalone | DOT | 60s | 5m | [115 empty] | Y
Relative_Power_Headroom | Metric | Power |  | Relative_Power_Headroom.AVG(5m) | For reporting purposes at room, floor, facility levels |  | Number | Variable Number | Ratio | PIT(2) | Intensive | Standalone | DOT | 5m | 5m | [84 empty] | Y | Y |  | Y
Relative_Power_Headroom | Metric | Power |  | Relative_Power_Headroom.P95(5m) | For reporting purposes at room, floor, facility levels |  | Number | Variable Number | Ratio | PIT(2) | Intensive | Standalone | DOT | 5m | 5m | [84 empty] | Y | Y |  | Y
Power_RampRate | Metric | Power | pwr_rr | Power_RampRate.60s | Used for rack and servers, reflecting local radpid changes | Rack | Number | Variable Number | Power per Time | PIT(2) | Intensive | Standalone | DOT | 5s | 60s | [80 empty] | Y | Y
Power_RampRate | Metric | Power | pwr_rr | Power_RampRate.120s | Used for rack and servers, reflecting local radpid changes | Rack | Number | Variable Number | Power per Time | PIT(2) | Intensive | Standalone | DOT | 5s | 120s | [80 empty] | Y | Y
Power_RampRate | Metric | Power |  | Power_RampRate.5m | for mid-level structures like UPS, Fabric, Pod, and for assessing thermal impacts at zone/ loop levels |  | Number | Variable Number | Power per Time | PIT(2) | Intensive | Standalone | DOT | 60s | 5m | [89 empty] | Y | [8 empty] | Y |  |  |  | Y | [6 empty] | Y | Y | [9 empty] | Y | [6 empty] | Y
Power_RampRate | Metric | Power |  | Power_RampRate.10m | for mid-level structures like UPS, Fabric, Pod, and for assessing thermal impacts at zone/ loop levels |  | Number | Variable Number | Power per Time | PIT(2) | Intensive | Standalone | DOT | 60s | 10m | [89 empty] | Y | [8 empty] | Y |  |  |  | Y | [6 empty] | Y | Y | [9 empty] | Y | [6 empty] | Y
Power_RampRate | Metric | Power |  | Power_RampRate.15m | For reporting purposes at room, floor, facility levels |  | Number | Variable Number | Power per Time | PIT(2) | Intensive | Standalone | DOT | 5m | 15m | [84 empty] | Y | Y |  | Y | [27 empty] | Y
Norm_Power_Increase | Metric | Power | pwr_inc_norm | Norm_Power_Increase |  | Rack | Number | Variable Number | Ratio | PIT(2) | Intensive | Standalone | DOT
Norm_Power_IncRate | Metric | Power | pwr_incr_norm | Norm_Power_IncRate |  | Rack | Number | Variable Number | Ratio per Time | PIT(2) | Intensive | Standalone | DOT
Power_JumpRating | Metric | Power | pwr_jpr | Power_JumpRating |  | Rack | Text | Variable Text |  |  | Intensive | Standalone | DOT
Power_SteepJump_Count | Metric | Power | pwr_sj_cnt | Power_SteepJump_Count.60s | for racks and servers | Rack | Number | Variable Number | Count | Interval | Extensive | Standalone | DOT | 5s | 60s | [80 empty] | Y | Y
Power_SteepJump_Count | Metric | Power | pwr_sj_cnt | Power_SteepJump_Count.5m | both rack, server, and zone, PDU, fabric domain, pod level monitoring | Rack | Number | Variable Number | Count | Interval | Extensive | Standalone | DOT | 5s | 5m | [80 empty] | Y | Y | [7 empty] | Y | [19 empty] | Y | Y | [9 empty] | Y | [6 empty] | Y
Power_SteepJump_Count | Metric | Power |  | Power_SteepJump_Count.15m | zone, PDU, fabric, Pod monitoring, and reporting at room or facility levels |  | Number | Variable Number | Count | Interval | Intensive | Standalone | DOT | 5m | 15m | [89 empty] | Y | [19 empty] | Y | Y | [9 empty] | Y | [6 empty] | Y
Power_Burstiness | Metric | Power | pwr_burst | Power_Burstiness.60s | for racks and servers | Rack | Number | Variable Number | Ratio per Time | PIT(2) | Intensive | Standalone | DOT | 5s | 60s | [80 empty] | Y | Y
Power_Burstiness | Metric | Power | pwr_burst | Power_Burstiness.5m | both rack, server, and zone, PDU, fabric domain, pod level monitoring | Rack | Number | Variable Number | Ratio per Time | PIT(2) | Intensive | Standalone | DOT | 5s | 5m | [80 empty] | Y | Y | [7 empty] | Y | [19 empty] | Y | Y | [9 empty] | Y | [6 empty] | Y
Power_Burstiness | Metric | Power |  | Power_Burstiness.15m | zone, PDU, fabric, Pod monitoring, and reporting at room or facility levels |  | Number | Variable Number | Ratio per Time | PIT(2) | Intensive | Standalone | DOT | 5m | 15m | [89 empty] | Y | [19 empty] | Y | Y | [9 empty] | Y | [6 empty] | Y
Power_Excess | Metric | Power | pwr_exc | Power_Excess |  | Rack, Server | Number | Variable Number | Ratio | PIT(2) | Intensive | Standalone | DOT
Power_Overlimit_Event | Event | Power |  | Power_Overlimit_Event |  | Rack, Server | Date Time | Variable Date Time |  |  |  | Standalone | SET | NA | NA | [80 empty] | Y | Y |  |  | Y | Y |  | Y |  | Y | [19 empty] | Y | Y |  |  |  |  | Y |  |  |  |  | Y | [6 empty] | Y
Power_Overlimit_Time | Metric | Power | pwr_ovrlim_time | Power_Overlimit_Time.60s |  | Rack | Number | Variable Number | Time | Interval | Intensive | Standalone | DOT | 5s/60s | 60s | [80 empty] | Y | Y |  |  | Y | Y |  | Y |  | Y | [19 empty] | Y | Y |  |  |  |  | Y |  |  |  |  | Y | [6 empty] | Y
Power_Overlimit_Time | Metric | Power | pwr_ovrlim_time | Power_Overlimit_Time.15m |  | Rack | Number | Variable Number | Time | Interval | Intensive | Standalone | DOT | 5s/60s | 15m | [80 empty] | Y | Y |  |  | Y | Y |  | Y |  | Y | [19 empty] | Y | Y |  |  |  |  | Y |  |  |  |  | Y | [6 empty] | Y
Relative_Power_Overshoot | Metric | Power | pwr_os_rel | Relative_Power_Overshoot.60s |  | Rack | Number | Variable Number | Ratio times Time | Interval | Intensive | Standalone | DOT | 5s/60s | 60s | [80 empty] | Y | Y |  |  | Y | Y |  | Y |  | Y | [19 empty] | Y | Y |  |  |  |  | Y |  |  |  |  | Y | [6 empty] | Y
Relative_Power_Overshoot | Metric | Power | pwr_os_rel | Relative_Power_Overshoot.15m |  | Rack | Number | Variable Number | Ratio times Time | Interval | Intensive | Standalone | DOT | 5s/60s | 15m | [80 empty] | Y | Y |  |  | Y | Y |  | Y |  | Y | [19 empty] | Y | Y |  |  |  |  | Y |  |  |  |  | Y | [6 empty] | Y
Power_Overshoot | Metric | Power | pwr_os | Power_Overshoot.60s |  | Rack | Number | Variable Number | Power times Time | Interval | Intensive | Standalone | DOT | 5s/60s | 60s | [80 empty] | Y | Y |  |  | Y | Y |  | Y |  | Y | [19 empty] | Y | Y |  |  |  |  | Y |  |  |  |  | Y | [6 empty] | Y
Power_Overshoot | Metric | Power | pwr_os | Power_Overshoot.15m |  | Rack | Number | Variable Number | Power times Time | Interval | Intensive | Standalone | DOT | 5s/60s | 15m | [80 empty] | Y | Y |  |  | Y | Y |  | Y |  | Y | [19 empty] | Y | Y |  |  |  |  | Y |  |  |  |  | Y | [6 empty] | Y
Temperature | Input | Thermal | temp | Temperature.InletTop |  | Rack | Number | Variable Number | Temperature | PIT(2) | Intensive | Standalone | DOT | [82 empty] | Y
Temperature | Input | Thermal | temp | Temperature.InletMid |  | Rack | Number | Variable Number | Temperature | PIT(2) | Intensive | Standalone | DOT | [82 empty] | Y
Temperature | Input | Thermal | temp | Temperature.InletBottom |  | Rack | Number | Variable Number | Temperature | PIT(2) | Intensive | Standalone | DOT | [82 empty] | Y
Temperature | Input | Thermal | tmp_op | Temperature.Inlet | tempereture of air entering IT system, for racks, servers, and air zones | Rack, Server | Number | Variable Number | Temperature | PIT(2) | Intensive | Standalone | DOT | [82 empty] | Y | Y | [16 empty] | Y
Temperature | Input | Thermal |  | Temperature.ambient | temperature or average temperature in larger facility areas |  | Number | Variable Number | Temperature | PIT(2) | Intensive | Standalone | DOT | [86 empty] | Y | Y |  | Y
Thermal_Limit | Reference | Thermal | thm_lim | Thermal_Limit |  | Rack, Server | Number | Variable Number | Temperature | PIT(2) | Intensive | Standalone | SET | [82 empty] | Y | Y | [16 empty] | Y
Thermal_Headroom | Metric | Thermal | thm_hdr | Thermal_Headroom | thermal headroom is for racks, servers, and air zones | Rack, Server | Number | Variable Number | Temperature | PIT(2) | Intensive | Standalone | DOT | 30s | [81 empty] | Y | Y | [16 empty] | Y
Thermal_Headroom | Metric | Thermal | thm_hdr | Thermal_Headroom.MIN(2m) | thermal headroom is for racks, servers, and air zones | Rack, Server | Number | Variable Number | Temperature | PIT(2) | Intensive | Standalone | DOT | 30s | 2m | [80 empty] | Y | Y | [16 empty] | Y
Thermal_Headroom | Metric | Thermal | thm_hdr | Thermal_Headroom.MIN(5m) | thermal headroom is for racks, servers, and air zones | Rack, Server | Number | Variable Number | Temperature | PIT(2) | Intensive | Standalone | DOT | 30s | 5m | [80 empty] | Y | Y | [16 empty] | Y
Thermal_Headroom | Metric | Thermal | thm_hdr | Thermal_Headroom.MIN(10m) | obsolete | [8 empty] | 30s | 10m
Thermal_Headroom | Metric | Thermal | thm_hdr | Thermal_Headroom.MIN(30m) | obsolete | [8 empty] | 30s | 30m
Thermal_Coupling | Metric | Thermal | thm_cpl | Thermal_Coupling.10m |  | Rack | Number | Variable Number | Temperature per Power | PIT(2) | Intensive | Standalone | DOT | 60s | 10m | [80 empty] | Y
Thermal_Coupling | Metric | Thermal | thm_cpl | Thermal_Coupling.30m |  | Rack | Number | Variable Number | Temperature per Power | PIT(2) | Intensive | Standalone | DOT | 60s | 30m | [80 empty] | Y
Thermal_Coupling | Metric | Thermal | thm_cpl | Thermal_Coupling.24h |  | Rack | Number | Variable Number | Temperature per Power | PIT(2) | Intensive | Standalone | DOT | 15m | 24h | [80 empty] | Y
Local_Temp_Diff | Metric | Thermal | tmp_diff_loc | Local_Temp_Diff |  | Rack | Number | Variable Number | Temperature | PIT(2) | Intensive | Standalone | DOT | [82 empty] | Y
Local_Temp_Diff | Metric | Thermal | tmp_diff_loc | Local_Temp_Diff.MAX(2m) |  |  | Number | Variable Number | Temperature | PIT(2) | Intensive | Standalone | DOT | 30s | 2m | [80 empty] | Y
Local_Temp_Diff | Metric | Thermal | tmp_diff_loc | Local_Temp_Diff.MAX(5m) |  |  | Number | Variable Number | Temperature | PIT(2) | Intensive | Standalone | DOT | 30s | 5m | [80 empty] | Y
Local_Temp_Diff | Metric | Thermal | tmp_diff_loc | Local_Temp_Diff.MAX(10m) | obsolete | Rack | Number | Variable Number | Temperature | PIT(2) | Intensive | Standalone
Local_Temp_Diff | Metric | Thermal | tmp_diff_loc | Local_Temp_Diff.MAX(30m) | obsolete | Rack | Number | Variable Number | Temperature | PIT(2) | Intensive | Standalone
Thermal_Excess | Metric | Thermal | thm_exc | Thermal_Excess |  | Rack, Server | Number | Variable Number | Temperature | PIT(2) | Intensive | Standalone | DOT
Thermal_Overheat_Event | Event | Thermal |  | Thermal_Overheat_Event |  | Rack, Server | Date Time | Variable Date Time |  |  |  | Standalone | SET | NA | NA | [80 empty] | Y | Y | [16 empty] | Y
Thermal_Overheat_Time | Metric | Thermal |  | Thermal_Overheat_Time.5m |  |  | Number | Variable Number | Time | Interval | Intensive | Standalone | DOT | 30s | 5m | [80 empty] | Y | Y | [16 empty] | Y
Thermal_Overheat_Time | Metric | Thermal | thm_oh_time | Thermal_Overheat_Time.10m |  | Rack, Server | Number | Variable Number | Time | Interval | Intensive | Standalone | DOT | 30s | 10m | [80 empty] | Y | Y | [16 empty] | Y
Thermal_Overheat_Time | Metric | Thermal | thm_oh_time | Thermal_Overheat_Time.15m | obsolete | Rack, Server | Number | Variable Number | Time | Interval | Intensive | Standalone
Temp_Overshoot | Metric | Thermal |  | Temp_Overshoot.15m |  |  | Number | Variable Number | Temperature times Time | Interval | Intensive | Standalone | DOT | 30s | 15m | [80 empty] | Y | Y | [16 empty] | Y
Temp_Overshoot | Metric | Thermal | tmp_os | Temp_Overshoot.30m |  | Rack, Server | Number | Variable Number | Temperature times Time | Interval | Intensive | Standalone | DOT | 30s | 30m | [80 empty] | Y | Y | [16 empty] | Y
Fan_Speed_Limit | Reference | Cooling | fan_spd_lim | Fan_Speed_Limit |  | Server | Number | Variable Number | Rotational Speed | PIT(2) | Intensive | Standalone | SET | [83 empty] | Y
Fan_Speed | Input | Cooling | fan_spd | Fan_Speed |  | Server | Number | Variable Number | Rotational Speed | PIT(2) | Intensive | Standalone | DOT | [83 empty] | Y
Fan_Saturation | Metric | Cooling | fan_sat | Fan_Saturation.AVG(30s) |  | Server | Number | Variable Number | Ratio | PIT(2) | Intensive | Standalone | DOT | 30s | 30s | [81 empty] | Y
Liquid_SupplyTemp | Input | Cooling | liq_sup_t | Liquid_SupplyTemp |  | LiquidLoop | Number | Variable Number | Temperature | PIT(2) | Intensive | Standalone | DOT | [104 empty] | Y
Liquid_ReturnTemp | Input | Cooling | liq_ret_t | Liquid_ReturnTemp |  | Liquid Loop | Number | Variable Number | Temperature | PIT(2) | Intensive | Standalone | DOT | [104 empty] | Y
Liquid_SupplyT_Limit | Reference | Cooling | liq_sup_t_lim | Liquid_SupplyT_Limit |  | Liquid Loop | Number | Variable Number | Temperature | PIT(2) | Intensive | Standalone | SET | [104 empty] | Y
Liquid_SupplyT_Margin | Metric | Cooling | liq_sup_t_mg | Liquid_SupplyT_Margin |  | Liquid Loop | Number | Variable Number | Temperature | PIT(2) | Intensive | Standalone | DOT | 30s | [103 empty] | Y
Liquid_SupplyT_Margin | Metric | Cooling | liq_sup_t_mg | Liquid_SupplyT_Margin.MIN(10m) |  | Liquid Loop | Number | Variable Number | Temperature | PIT(2) | Intensive | Standalone | DOT | 30s | 10m | [102 empty] | Y
Liquid_SupplyT_Margin | Metric | Cooling | liq_sup_t_mg | Liquid_SupplyT_Margin.MIN(30m) |  | Liquid Loop | Number | Variable Number | Temperature | PIT(2) | Intensive | Standalone | DOT | 30s | 30m | [102 empty] | Y
Liquid_ReturndT_perkW | Metric | Cooling | liq_ret_dt_kw | Liquid_ReturndT_perkW.10m |  | Liquid Loop | Number | Variable Number | Temperature per Power | PIT(2) | Intensive | Standalone | DOT | 30s | 10m | [102 empty] | Y
Liquid_ReturndT_perkW | Metric | Cooling | liq_ret_dt_kw | Liquid_ReturndT_perkW.30m |  | Liquid Loop | Number | Variable Number | Temperature per Power | PIT(2) | Intensive | Standalone | DOT | 30s | 30m | [102 empty] | Y
Pump_Speed | Input | Cooling | pump_spd | Pump_Speed.5m |  | Liquid Loop | Number | Variable Number | Rotational Speed | PIT(2) | Intensive | Standalone | DOT
Pump_Speed_Limit | Reference | Cooling | pump_spd_lim | Pump_Speed_Limit |  | Liquid Loop | Number | Variable Number | Rotational Speed | PIT(2) | Intensive | Standalone | SET
Pump_Control_Percent | Input | Cooling | pump_ctrl_pct | Pump_Control_Percent.P(n) |  | Liquid Loop | Number | Variable Number | Ratio | PIT(2) | Intensive | Standalone | DOT | [104 empty] | Y
Pump_Saturation | Input | Cooling | pump_sat | Pump_Saturation.P(n) |  | Liquid Loop | Number | Variable Number | Ratio | PIT(2) | Intensive | Standalone | DOT | [104 empty] | Y
Pump_Saturation | Input | Cooling | pump_sat | Pump_Saturation.P(n).5m |  | Liquid Loop | Number | Variable Number | Ratio | PIT(2) | Intensive | Standalone | DOT | [104 empty] | Y
Pump_Saturation | Metric | Cooling | pump_sat | Pump_Saturation.MAX.5m |  | Liquid Loop | Number | Variable Number | Ratio | PIT(2) | Intensive | Standalone | DOT | 30s | 5m | [102 empty] | Y
Air_SupplyTemp | Input |  |  | Air_SupplyTemp | [8 empty] | DOT | [100 empty] | Y
Air_ReturnTemp | Input |  |  | Air_ReturnTemp | [8 empty] | DOT | [100 empty] | Y
Air_SupplyT_Limit | Input |  |  | Air_SupplyT_Limit | [8 empty] | SET | [100 empty] | Y
Air_SupplyT_Margin | Input |  |  | Air_SupplyT_Margin | [8 empty] | DOT | [100 empty] | Y
Breaker_Headroom | Metric | Power | brk_hdr | Breaker_Headroom |  | Switchgear, PDU/ RPP, Rack PDU | Number | Variable Number | Power | PIT(2) | Intensive | Standalone | DOT | [106 empty] | Y |  | Y |  | Y |  | Y | Y |  |  | Y | Y | Y
Breaker_Headroom | Metric | Power | brk_hdr | Breaker_Headroom.MIIN(30s) | for Rack PDU | Switchgear, PDU/ RPP, Rack PDU | Number | Variable Number | Power | PIT(2) | Intensive | Standalone | DOT | 5s | 30s | [111 empty] | Y
Breaker_Headroom | Metric | Power |  | Breaker_Headroom.AVG(2m) | for Rack PDU, Captures sustained near-overload without being too sticky; ramps are still relevant. |  | Number | Variable Number | Power | PIT(2) | Intensive | Standalone | DOT | 5s | 2m | [111 empty] | Y
Breaker_Headroom | Metric | Power |  | Breaker_Headroom.AVG(5m) | for PDU, Good default for feeder protection behavior and thermal inertia. for BESS |  | Number | Variable Number | Power | PIT(2) | Intensive | Standalone | DOT | 5s | 5m | [104 empty] | Y |  | Y |  |  |  | Y
Breaker_Headroom | Metric | Power |  | Breaker_Headroom.AVG(10m) | for mechanical power panel, UPS, and switch gear |  | Number | Variable Number | Power | PIT(2) | Intensive | Standalone | DOT | 5s | 10m | [108 empty] | Y | [5 empty] | Y | Y
Min_Headroom_UpstreamBreaker | Metric | Power | min_hdr_upbrk | Min_Headroom_UpstreamBreaker.FeedA.30s |  | Rack | Number | Variable Number | Power | PIT(2) | Intensive | Standalone | DOT
Min_Headroom_UpstreamBreaker | Metric | Power | min_hdr_upbrk | Min_Headroom_UpstreamBreaker.FeedB.30s |  | Rack | Number | Variable Number | Power | PIT(2) | Intensive | Standalone | DOT
MinPower_Headroom_UpstreamBreaker | Metric | Power | pwr_hdr_min_upbrk | Min_Headroom_UpstreamBreaker.30s |  | Rack | Number | Variable Number | Power | PIT(2) | Intensive | Standalone | DOT | 5s | 30s | [80 empty] | Y | Y | [7 empty] | Y | [30 empty] | Y | [6 empty] | Y
Power_Peak_Probability | Metric | Power | pwr_peak_prob | Power_Peak_Probability.1m |  | Rack, Server | Number | Variable Number | Ratio | PIT(2) | Intensive | Standalone | DOT | 5s | 1m | [80 empty] | Y | Y | [7 empty] | Y | [30 empty] | Y | [6 empty] | Y
Power_Peak_Probability | Metric | Power | pwr_peak_prob | Power_Peak_Probability.5m |  | Rack, Server | Number | Variable Number | Ratio | PIT(2) | Intensive | Stand alone | DOT | 5s | 5m | [80 empty] | Y | Y | [7 empty] | Y | [30 empty] | Y | [6 empty] | Y
Power_Usage_Std | Metric | Power |  | Power_Usage_Std.2m |  | Server | Number | Variable Number | Dimensionless | PIT(2) | Intensive | Stand alone | DOT | 5s | 2m
Power_Headroom_Factor | Metric | Power | pwr_hdr_fac | Power_Headroom_Factor |  | Rack, Server | Number | Variable Number | Dimensionless | PIT(2) | Intensive | Stand alone | SET | [82 empty] | Y | Y
Power_RampRate_Factor | Metric | Power | pwr_rr_fac | Power_RampRate_Factor |  | Rack | Number | Variable Number | Dimensionless | PIT(2) | Intensive | Stand alone | SET | [82 empty] | Y
Power_Burstiness_Factor | Metric | Power | pwr_burst_fac | Power_Burstiness_Factor |  | Rack | Number | Variable Number | Dimensionless | PIT(2) | Intensive | Stand alone | SET | [82 empty] | Y
Power_PeakRisk_Factor | Metric | Power | pwr_peakrisk_fac | Power_PeakRisk_Factor |  | Rack | Number | Variable Number | Dimensionless | PIT(2) | Intensive | Stand alone | SET | [82 empty] | Y | Y
Power_Overlimit_Factor | Metric | Power | pwr_overlim_fac | Power_Overlimit_Factor |  | Rack, Server | Number | Variable Number | Dimensionless | PIT(2) | Intensive | Stand alone | SET | [82 empty] | Y | Y
Thermal_Headroom_Factor | Metric | Thermal | thm_hdr_fac | Thermal_Headroom_Factor |  | Rack, Server | Number | Variable Number | Dimensionless | PIT(2) | Intensive | Stand alone | SET | [82 empty] | Y | Y
Thermal_Hotspot_Factor | Metric | Thermal | thm_hspt_fac | Thermal_Hotspot_Factor |  | Rack | Number | Variable Number | Dimensionless | PIT(2) | Intensive | Stand alone | SET | [82 empty] | Y
Thermal_Overheat_Factor | Metric | Thermal | thm_oh_fac | Thermal_Overheat_Factor |  | Rack, Server | Number | Variable Number | Dimensionless | PIT(2) | Intensive | Stand alone | SET | [82 empty] | Y | Y
Thermal_Coupling_Factor | Metric | Thermal | thm_cpl_fac | Thermal_Coupling_Factor |  | Rack | Number | Variable Number | Dimensionless | PIT(2) | Intensive | Stand alone | SET | [82 empty] | Y
Cooling_Efficiency_Factor | Metric | Cooling | cool_eff_fac | Cooling_Efficiency_Factor |  | Rack | Number | Variable Number | Dimensionless | PIT(2) | Intensive | Stand alone | SET | [82 empty] | Y
Fan_Saturation_Factor | Metric | Cooling | fan_sac_fac | Fan_Saturation_Factor |  | Server | Number | Variable Number | Dimensionless | PIT(2) | Intensive | Stand alone | SET | [83 empty] | Y
Liquid_SupplyT_Margin_Factor | Metric | Cooling | liq_sup_t_mg_fac | Liquid_SupplyT_Margin_Factor |  | Liquid Loop | Number | Variable Number | Dimensionless | PIT(2) | Intensive | Stand alone | SET | [104 empty] | Y
Liquid_ReturndT_perkW_Factor | Metric | Cooling | liq_ret_dt_kw_fac | Liquid_ReturndT_perkW_Factor |  | Liquid Loop | Number | Variable Number | Dimensionless | PIT(2) | Intensive | Stand alone | SET | [104 empty] | Y
Pump_Saturation_Factor | Metric | Cooling | pump_sac_fac | Pump_Saturation_Factor |  | Liquid Loop | Number | Variable Number | Dimensionless | PIT(2) | Intensive | Stand alone | SET | [104 empty] | Y
UpstreamBreaker_Headroom_Factor | Metric | Power | pwr_hdr_up_brk_fac | UpstreamBreaker_Headroom_Factor |  | Rack | Number | Variable Number | Dimensionless | PIT(2) | Intensive | Stand alone | SET | [82 empty] | Y
Batchability_PowerProxy_Factor | Metric | Compute | batch_pwrproxy_fac | Batchability_PowerProxy_Factor |  | Server | Number | Variable Number | Dimensionless | PIT(2) | Intensive | Stand alone | SET | [120 empty] | Y
Power_Headroom_wt | Reference | Power | pwr_hdr_wt | Power_Headroom_wt |  | Rack, Server | Number | Variable Number | Dimensionless | PIT(2) | Intensive | Stand alone | SET | [82 empty] | Y | Y
Power_RampRate_wt | Reference | Power | pwr_rr_wt | Power_RampRate_wt |  | Rack | Number | Variable Number | Dimensionless | PIT(2) | Intensive | Stand alone | SET | [82 empty] | Y
Power_Burstiness_wt | Reference | Power | pwr_burst_wt | Power_Burstiness_wt |  | Rack | Number | Variable Number | Dimensionless | PIT(2) | Intensive | Stand alone | SET | [82 empty] | Y
Power_PeakRisk_wt | Reference | Power | pwr_peakrisk_wt | Power_PeakRisk_wt |  | Rack | Number | Variable Number | Dimensionless | PIT(2) | Intensive | Stand alone | SET | [82 empty] | Y | Y
Power_Overlimit_wt | Reference | Power | pwr_overlim_wt | Power_Overlimit_wt |  | Rack, Server | Number | Variable Number | Dimensionless | PIT(2) | Intensive | Stand alone | SET | [82 empty] | Y | Y
Thermal_Headroom_wt | Reference | Thermal | thm_hdr_wt | Thermal_Headroom_wt |  | Rack, Server | Number | Variable Number | Dimensionless | PIT(2) | Intensive | Stand alone | SET | [82 empty] | Y | Y
Thermal_Hotspot_wt | Reference | Thermal | thm_hspt_wt | Thermal_Hotspot_wt |  | Rack | Number | Variable Number | Dimensionless | PIT(2) | Intensive | Stand alone | SET | [82 empty] | Y
Thermal_Overheat_wt | Reference | Thermal | thm_oh_wt | Thermal_Overheat_wt |  | Rack, Server | Number | Variable Number | Dimensionless | PIT(2) | Intensive | Stand alone | SET | [82 empty] | Y | Y
Thermal_Coupling_wt | Reference | Thermal | thm_cpl_wt | Thermal_Coupling_wt |  | Rack | Number | Variable Number | Dimensionless | PIT(2) | Intensive | Stand alone | SET | [82 empty] | Y
Cooling_Efficiency_wt | Reference | Cooling | cool_eff_wt | Cooling_Efficiencty_wt |  | Rack | Number | Variable Number | Dimensionless | PIT(2) | Intensive | Stand alone | SET | [82 empty] | Y
Fan_Saturation_wt | Reference | Cooling | fan_sac_wt | Fan_Saturation_wt |  | Server | Number | Variable Number | Dimensionless | PIT(2) | Intensive | Stand alone | SET | [83 empty] | Y
Liquid_SupplyT_Margin_wt | Reference | Cooling | liq_sup_t_mg_wt | Liquid_SupplyT_Margin_wt |  | Liquid Loop | Number | Variable Number | Dimensionless | PIT(2) | Intensive | Stand alone | SET | [104 empty] | Y
Liquid_ReturndT_perkW_wt | Reference | Cooling | liq_ret_dt_kw_wt | Liquid_ReturndT_perkW_wt |  | Liquid Loop | Number | Variable Number | Dimensionless | PIT(2) | Intensive | Stand alone | SET | [104 empty] | Y
Pump_Saturation_wt | Reference | Cooling | pump_sac_wt | Pump_Saturation_wt |  | Liquid Loop | Number | Variable Number | Dimensionless | PIT(2) | Intensive | Stand alone | SET | [104 empty] | Y
UpstreamBreaker_Headroom_wt | Reference | Power | pwr_hdr_up_brk_wt | UpstreamBreaker_Headroom_wt |  | Rack | Number | Variable Number | Dimensionless | PIT(2) | Intensive | Stand alone | SET | [82 empty] | Y
Batchability_PowerProxy_wt | Reference | Compute | batch_pwrproxy_wt | Batchability_PowerProxy_wt |  | Compute Node | Number | Variable Number | Dimensionless | PIT(2) | Intensive | Stand alone | SET | [120 empty] | Y
Power_Fitness_Index | Metric | Power | pwr_fit_idx | Power_Fitness_Index |  | Rack, Server | Number | Variable Number | Dimensionless | PIT(2) | Intensive | Stand alone | SET | [82 empty] | Y | Y
Thermal_Fitness_Index | Metric | Thermal | thm_fit_idx | Thermal_Fitness_Index |  | Rack, Server | Number | Variable Number | Dimensionless | PIT(2) | Intensive | Stand alone | SET | [82 empty] | Y | Y
Cooling_Efficiency_Index | Metric | Cooling | cool_fit_idx | Cooling_Efficiency_Index |  | Rack | Number | Variable Number | Dimensionless | PIT(2) | Intensive | Stand alone | SET | [82 empty] | Y
LiquidCooling_Fitness_Index | Metric | Cooling | liqcool_fit_idx | LiquidCooling_Fitness_Index |  | Liquid Loop | Number | Variable Number | Dimensionless | PIT(2) | Intensive | Stand alone | SET | [104 empty] | Y
Upstream_PowerRisk_Index | Metric | Power | pwr_risk_up_idx | Upstream_PowerRisk_Index |  | Rack | Number | Variable Number | Dimensionless | PIT(2) | Intensive | Stand alone | SET | [82 empty] | Y
Batching_Fitness_Index | Metric | Compute | batch_fit_idx | Batching_Fitness_Index |  | Compute Node | Number | Variable Number | Dimensionless | PIT(2) | Intensive | Stand alone | SET | [120 empty] | Y
Power_Fitness_Index_wt | Reference | Power | pwr_fit_wt | Power_Fitness_Index_wt |  | Rack, Server | Number | Variable Number | Dimensionless | PIT(2) | Intensive | Stand alone | SET | [82 empty] | Y | Y
Thermal_Fitness_Index_wt | Reference | Thermal | thm_fit_wt | Thermal_Fitness_Index_wt |  | Rack, Server | Number | Variable Number | Dimensionless | PIT(2) | Intensive | Stand alone | SET | [82 empty] | Y | Y
Cooling_Efficiency_Index_wt | Reference | Cooling | cool_fit_wt | Cooling_Efficiency_Index_wt |  | Rack | Number | Variable Number | Dimensionless | PIT(2) | Intensive | Stand alone | SET | [82 empty] | Y
LiquidCooling_Fitness_Index_wt | Reference | Cooling | liqcool_fit_wt | LiquidCooling_Fitness_Index_wt |  | Liquid Loop | Number | Variable Number | Dimensionless | PIT(2) | Intensive | Stand alone | SET | [104 empty] | Y
Upstream_PowerRisk_Index_wt | Reference | Power | pwr_risk_up_wt | Upstream_PowerRisk_Index_wt |  | Rack | Number | Variable Number | Dimensionless | PIT(2) | Intensive | Stand alone | SET | [82 empty] | Y
Batching_Fitness_Index_wt | Reference | Compute | batch_fit_wt | Batching_Fitness_Index_wt |  | Compute Node | Number | Variable Number | Dimensionless | PIT(2) | Intensive | Stand alone | SET | [120 empty] | Y
Node_Fitness_Index | Metric | Composite |  | Node_Fitness_Index |  | Compute Node | Number | Variable Number | Dimensionless | PIT(2) | Intensive | Stand alone | DOT | 5s | last available input | [118 empty] | Y
GPU_Count | Reference |  |  | GPU_Count | [8 empty] | SET | [82 empty] | Y | Y | [36 empty] | Y |  | Y | [6 empty] | Y
GPU_Utilization | Metric |  |  | GPU_Utilization | [8 empty] | DOT | [82 empty] | Y | Y | [36 empty] | Y |  | Y | [6 empty] | Y
PUE | Metric |  |  | PUE | [8 empty] | DOT | [87 empty] | Y
| Reference |  |  | Rack_Circuit_Capacity_(rated) | The rack capacity limit imposed by the branch circuit breaker from RPP, before derating | [90 empty] | Y
| Reference |  |  | Rack_Circuit_Capacity_(design) | The rack capacity limit imposed by the branch circuit breaker from RPP, after applying a derating factor, often 80% |  | Number | Constant Number | Power | PIT(2) | Extensive | Standard Rollup | [5 empty] | Y | [77 empty] | Y |  |  |  | Y | Y |  | Y |  | Y | Y | [38 empty] | Y | Y | Y | Y | Y | Y | Y | Y
| Input |  |  | Allocated_ITLoad | The kW load that is allocated to racks |  | Number | Constant Number | Power | PIT(2) | Extensive | Standard Rollup | [5 empty] | Y |  | Y | Y | [74 empty] | Y |  |  |  | Y | Y |  | Y |  | Y | Y |  | Y | [5 empty] | Y | Y | Y |  | Y |  | Y |  | Y |  |  | Y | Y |  |  |  | Y | Y | Y | [15 empty] | Y | Y | Y | Y | Y
| Input |  |  | TheorMax_ITLoad | The sum of peak load for each device in the rack is hte maximum theoretical IT load |  | Number | Constant Number | Power | PIT(2) | Extensive | Standard Rollup | [5 empty] | Y |  | Y | Y | [74 empty] | Y |  |  |  | Y | Y |  | Y |  | Y | Y |  | Y | [5 empty] | Y | Y | Y |  | Y |  | Y |  | Y |  |  | Y | Y |  |  |  | Y | Y | Y | [15 empty] | Y | Y | Y | Y | Y
| Reference |  |  | Rack_AirCool_Fraction | the fraction of heat desgined to be removed by air |  | Number | Constant Number | Ratio | PIT(2) | Intensive | Stand alone
| Reference |  |  | Rack_LiquidCool_Fraction | the fraction of heat desgined to be removed by liquid cooling |  | Number | Constant Number | Ratio | PIT(2) | Intensive | Stand alone
| Metric |  |  | Allocated_AirCool_Load |  |  | Number | Constant Number | Power | PIT(2) | Extensive | Standard Rollup | [7 empty] | Y |  |  |  | Y | Y | [70 empty] | Y | [17 empty] | Y | Y | Y |  | Y | [26 empty] | Y | Y | Y | Y | Y | Y | Y | Y
| Metric |  |  | Allocated_LiquidCool_Load |  |  | Number | Constant Number | Power | PIT(2) | Extensive | Standard Rollup | [7 empty] | Y |  |  |  | Y | Y | [70 empty] | Y | [17 empty] | Y | Y | Y |  | Y | [26 empty] | Y | Y | Y | Y | Y | Y | Y | Y
| Metric |  |  | TheorMax_AirCool_Load |  |  | Number | Constant Number | Power | PIT(2) | Extensive | Standard Rollup | [7 empty] | Y |  |  |  | Y | Y | [70 empty] | Y | [17 empty] | Y | Y | Y |  | Y | [26 empty] | Y | Y | Y | Y | Y | Y | Y | Y
| Metric |  |  | TheorMax_LiquidCool_Load |  |  | Number | Constant Number | Power | PIT(2) | Extensive | Standard Rollup | [7 empty] | Y |  |  |  | Y | Y | [70 empty] | Y | [17 empty] | Y | Y | Y |  | Y | [26 empty] | Y | Y | Y | Y | Y | Y | Y | Y
| Metric |  |  | Local_Capacity_Margin | local to each capacity node, calculated by the Capacity cap - Allocated IT Load |  | Number | Constant Number | Power | PIT(2) | Extensive | Stand alone | [83 empty] | Y | [17 empty] | Y | Y | Y |  | Y |  |  |  | Y |  |  | Y | [5 empty] | Y
| Metric |  |  | Local_Capacity_Margin% |  |  | Number | Constant Number | Ratio | PIT(2) | Intensive | Stand alone | [83 empty] | Y | [17 empty] | Y | Y | Y |  | Y |  |  |  | Y |  |  | Y | [5 empty] | Y
| Metric |  |  | Device_Capacity_Margin | specific to the device, calculated by the device's design capacith - allocated It load |  | Number | Constant Number | Power | PIT(2) | Extensive | Stand alone | [112 empty] | Y | Y
| Metric |  |  | Device_Capacity_Margin% |  |  | Number | Constant Number | Ratio | PIT(2) | Intensive | Stand alone | [112 empty] | Y | Y
| Metric |  |  | Upstream_Capacity_Margin |  |  | Number | Constant Number | Power | PIT(2) | Extensive | Stand alone | [83 empty] | Y | Y | Y | Y | [14 empty] | Y | Y |  | Y | Y | Y | [5 empty] | Y | Y |  |  |  |  | Y
| Metric |  |  | Upstream_Capacity_Margin% |  |  | Number | Constant Number | Ratio | PIT(2) | Intensive | Stand alone | [83 empty] | Y | Y | Y | Y | [14 empty] | Y | Y |  | Y | Y | Y | [5 empty] | Y | Y |  |  |  |  | Y
| Metric |  |  | Rack_Count |  |  | Number | Constant Number | Count | PIT(2) | Extensive | Standard Rollup | [5 empty] | Y |  | Y | Y | [74 empty] | Y |  |  |  | Y | Y |  | Y |  | Y | Y |  | Y | [5 empty] | Y | Y | Y |  | Y |  | Y |  | Y |  |  | Y | Y |  |  |  | Y | Y | Y | [15 empty] | Y | Y | Y | Y | Y
| Reference |  |  | Rated_Cooling_Capacity |  |  | Number | Constant Number | Power | PIT(2) | Extensive | Stand alone | [95 empty] | Y | Y
| Reference |  |  | Pump_Capacity |  |  | Number | Constant Number | Flow Rate | PIT(2) | Intensive | Stand alone | [96 empty] | Y
| Reference |  |  | RPP_Panel_Capacity_(rated) |  |  | Number | Constant Number | Power | PIT(2) | Extensive | Stand alone | [113 empty] | Y
| Reference |  |  | RPP_Panel_Capacity_(design) | RPP panel capacity (rated) after applying derating |  | Number | Constant Number | Power | PIT(2) | Extensive | Stand alone | [113 empty] | Y | [18 empty] | Y | Y | Y | Y | Y | Y | Y | Y
| Reference |  |  | RPP_BreakerPole_Capacity |  |  | Number | Constant Number | Count | PIT(2) | Extensive | Stand alone | [113 empty] | Y
| Reference |  |  | AirZone_Cooling_Capacity |  |  | Number | Constant Number | Power | PIT(2) | Extensive | Stand alone | [132 empty] | Y | Y | Y | Y | Y | Y | Y | Y
| Reference |  |  | Maximum_Air_Flow |  |  | Number | Constant Number | Flow Rate | PIT(2) | Intensive | Stand alone | [95 empty] | Y | [5 empty] | Y
| Reference |  |  | Rack_Inlet_Setpoint | arget temperature at the server inlet used for control and alarms. |  | Number | Constant Number | Temperature | PIT(2) | Intensive | Stand alone | [101 empty] | Y
| Reference |  |  | ColdAisle_Supply_Temp | emperature of air delivered into the cold aisle from the cooling system. |  | Number | Constant Number | Temperature | PIT(2) | Intensive | Stand alone | [101 empty] | Y
| Reference |  |  | Rack_DeltaT_(design) | design temperature rise across the rack: inlet → exhaust. |  | Number | Constant Number | Temperature | PIT(2) | Intensive | Stand alone | [101 empty] | Y
| Reference |  |  | LL_Cooling_Capacity |  |  | Number | Constant Number | Power | PIT(2) | Extensive | Stand alone
| Reference |  |  | Loop_Supply_Setpoint | coolant temperature delivered from the CDU to the rack liquid loop. |  | Number | Constant Number | Temperature | PIT(2) | Intensive | Stand alone | [105 empty] | Y
| Reference |  |  | Loop_DeltaT_(design) | return minus supply |  | Number | Constant Number | Temperature | PIT(2) | Intensive | Stand alone | [105 empty] | Y
| Reference |  |  | RPDU_Transformer_Rating | Nameplate capacity of the RPDU transformer (kVA or kW). |  | Number | Constant Number | Power | PIT(2) | Extensive | Stand alone | [112 empty] | Y
| Reference |  |  | RPDU_Design_Capacity | Transformer rating × engineering derating (e.g., thermal margin, continuous load assumptions). |  | Number | Constant Number | Power | PIT(2) | Extensive | Stand alone | [112 empty] | Y
| Reference |  |  | RPDU_Operational_Cap | Planning envelope used by operators to control deployment. Often lower than design capacity to preserve redundancy or growth margin. |  | Number | Constant Number | Power | PIT(2) | Extensive | Stand alone | [112 empty] | Y | [19 empty] | Y | Y | Y | Y | Y | Y | Y | Y
| Reference |  |  | UPS_Rated_Capacity | Nameplate maximum output of the UPS system/module configuration. This is the hard equipment rating. |  | Number | Constant Number | Power | PIT(2) | Extensive | Stand alone | [118 empty] | Y
| Reference |  |  | UPS_Design_Capacity | Rated capacity after any engineering derating or design assumptions. In some facilities this may equal the rated capacity, but in your model it is the local device-side usable capacity. |  | Number | Constant Number | Power | PIT(2) | Extensive | Stand alone | [118 empty] | Y
| Reference |  |  | UPS_Operational_Cap | The lower planning envelope operators use for deployment, redundancy, and growth margin. |  | Number | Constant Number | Power | PIT(2) | Extensive | Stand alone | [118 empty] | Y | [13 empty] | Y | Y | Y | Y | Y | Y | Y | Y
| Reference |  |  | RDHx_MaxHeat_Removal |  |  | Number | Constant Number | Power | PIT(2) | Extensive | Stand alone | [106 empty] | Y
| Reference |  |  | DTC_MaxCool_Capacity |  |  | Number | Constant Number | Power | PIT(2) | Extensive | Stand alone | [104 empty] | Y
| Metric |  |  | Capacity_Envelope | Capacity_Envelope = min(Power Capacity, Thermal Capacity) |  | Number | Constant Number | Power | PIT(2) | Extensive | Stand alone | [132 empty] | Y | Y | Y | Y | Y | Y | Y | Y
| Metric |  |  | Power_Capacity |  |  | Number | Constant Number | Power | PIT(2) | Extensive | Stand alone | [11 empty] | Y | Y | [119 empty] | Y | Y | Y | Y | Y | Y | Y | Y
| Metric |  |  | Thermal_Capacity |  |  | Number | Constant Number | Power | PIT(2) | Extensive | Stand alone | [11 empty] | Y | Y | [119 empty] | Y | Y | Y | Y | Y | Y | Y | Y
| Metric |  |  | Cell_Margin |  |  | Number | Constant Number | Power | PIT(2) | Extensive | Stand alone | [135 empty] | Y
| Metric |  |  | Cell_Margin% |  |  | Number | Constant Number | Ratio | PIT(2) | Intensive | Stand alone | [135 empty] | Y
| Metric |  |  | Cell_Utilization% |  |  | Number | Constant Number | Ratio | PIT(2) | Intensive | Stand alone | [135 empty] | Y
| Metric |  |  | Power_Margin |  |  | Number | Constant Number | Power | PIT(2) | Extensive | Stand alone | [132 empty] | Y | Y | Y | Y
| Metric |  |  | Power_Margin% |  |  | Number | Constant Number | Ratio | PIT(2) | Intensive | Stand alone | [132 empty] | Y | Y | Y | Y
| Metric |  |  | Thermal_Margin |  |  | Number | Constant Number | Power | PIT(2) | Extensive | Stand alone | [132 empty] | Y | Y | Y | Y
| Metric |  |  | Thermal_Margin% |  |  | Number | Constant Number | Ratio | PIT(2) | Intensive | Stand alone | [132 empty] | Y | Y | Y | Y
| Reference |  |  | Liquid_Cooling_Capacity | [110 empty] | Y
| Reference |  |  | Air_Cooling_Capacity | [110 empty] | Y
| Metric |  |  | Upstream_Capacity
| Metric |  |  | Upstream_Load
| Metric |  |  | Rack_Positions
| Reference |  |  | Facility_Deployable_ITCapacity

## NTList
Order | Node Type | Topology | Topology seq
1 | Server | Spatial | a
2 | Storage Device | Spatial | a
3 | Networking Device | Spatial | a
4 | Rack | Spatial | a
5 | Row | Spatial | a
6 | Aisle | Spatial | a
7 | Zone | Spatial | a
8 | Room | Spatial | a
9 | Floor | Spatial | a
10 | Electrical Room | Spatial | a
11 | Mechanical Room | Spatial | a
12 | Cooling Yard | Spatial | a
13 | Generator Yard | Spatial | a
14 | Transformer Yard | Spatial | a
15 | Roof | Spatial | a
16 | IT Facility | Spatial | a
17 | Site | Spatial | a
1 | Device PSU | Electrical | b
2 | Rack PDU Outlet | Electrical | b
3 | Rack PDU | Electrical | b
4 | RPP | Electrical | b
5 | Room PDU | Electrical | b
6 | UPS | Electrical | b
7 | BESS | Electrical | b
8 | Switch Gear | Electrical | b
9 | Generator | Electrical | b
10 | Transformer | Electrical | b
11 | Utility Feed | Electrical | b
12 | Lighting | Electrical | b
13 | Mechanical Power Panel | Electrical | b
1 | RDHx | Cooling System | c
2 | DTC | Cooling System | c
3 | Liquid Loop | Cooling System | c
4 | Air Zone | Cooling System | c
5 | CDU | Cooling System | c
6 | Air Cooling Unit | Cooling System | c
7 | Cooling Distribution | Cooling System | c
8 | Cooling Plant | Cooling System | c
9 | Chiller | Cooling System | c
10 | Condenser Chilled Water Pump | Cooling System | c
11 | Condenser Water Pump | Cooling System | c
12 | Cooling Tower Cell | Cooling System | c
1 | Capacity Cell | Whitespace | d
2 | Room Bundle | Whitespace | d
3 | Room PDU Bundle | Whitespace | d
4 | UPS Bundle | Whitespace | d
5 | Containment Bundles | Whitespace | d
1 | Deployment | Deployment | e
2 | Cluster | Deployment | e
3 | Placement Plan | Deployment | e
4 | Placement Draft | Deployment | e
1 | Fabric Domain | AI Infrastructure | f
2 | Inference Application | AI Infrastructure | f
3 | Compute Node | AI Infrastructure | f
4 | Job | AI Infrastructure | f
5 | Job Placement | AI Infrastructure | f
6 | Model | AI Infrastructure | f
7 | Model Replica | AI Infrastructure | f
8 | Queue | AI Infrastructure | f
9 | Project | AI Infrastructure | f
1 | Asset Class | Asset Inventory | g
2 | Asset Type | Asset Inventory | g
3 | ATS/ STS | Asset Inventory | g
4 | Secondary Pump | Asset Inventory | g
1 | Pod | Pod | h
1 | Business Unit | Operational | i
2 | Team | Operational | i
3 | Vendor | Operational | i

## Variables (hidden)
VariableType | Variable Class | Functional Domain | abbreviation | Variables: (VariableType.Modifier) | Description | Node Types | Data Format | Object Type | Unit Class | Variable Data Type | Extensivity | Data Topology | DOT/ SET | RFQ | RIT | SIT | C-SIT | Spatial | Operational Infrastructure | Cooling System | Electrical System | AI Infrastructure Fabric | Pod Operations | Whitespace | Deployment | Networking Device | Rack | Server | Storage Device | Business Unit | Floor | IT Facility | Project | Room | Team | Zone | Row | Aisle | Air Cooling Unit | CDU | Chiller | Condenser Chilled Water Pump | Condenser Water Pump | Cooling Tower Cell | Air Zone | Cooling Distribution | Cooling Plant | DTC | Liquid Loop | RDHx | BESS | Device PSU | Generator | Lighting | Mechanical Power Panel | Room PDU | RPP | Rack PDU | Rack PDU Outlet | Secondary Pump | Switch Gear | UPS | Utility Feed | Cluster | Compute Node | Deployment | Fabric Domain | Inference Application | Job | Job Placement | Model | Model Replica | Queue | Pod | Containment Bundles | Room Bundle | Room PDU Bundle | UPS Bundle | Capacity Cell | Deployment | Cluster | Placement Plan | Placement Draft
Power_Usage | Input | Power | pwr_use | Power_Usage |  | Rack, Server, Loop, Compute Node | Number | Variable Number | Power | PIT(2) | Extensive | Standard Rollup | DOT |  |  |  | 5s | Y | Y |  | Y | Y | Y | [34 empty] | T | T
Power_Flow | Input | Power |  | Power_Flow |  |  | Number | Variable Number | Power | PIT(2) | Extensive | Inclusive Flow |  |  |  |  | 5s |  |  |  | Y
Power_Input | Input | Power |  | Power_Input |  |  | Number | Variable Number | Power | PIT(2) | Extensive | Standalone | [38 empty] | Y |  |  |  | Y | Y | Y |  |  |  |  | Y
Power_Output | Input | Power |  | Power_Output |  |  | Number | Variable Number | Power | PIT(2) | Extensive | Standalone | [38 empty] | Y |  |  |  | Y | Y | Y |  |  |  |  | Y | Y
Power_Usage | Input | Power | pwr_use | Power_Usage.gpu(n) | The gpu power consumption are folded as variables into compute nodes | Compute Node | Number | Variable Number | Power | PIT(2) | Extensive | Standalone | [52 empty] | Y
Rated_Power_Capacity | Reference | Power | pwr_cap_rated | Rated_Power_Capacity | The maximum continuous power a component or system is designed and certified to handle under specified conditions | Rack | Number | Variable Number | Power | PIT(2) | Intensive | Standalone | [13 empty] | Y | Y | Y | Y | [21 empty] | Y | Y | Y |  | Y | Y | Y | Y |  |  | Y | Y
Power_Limit | Reference | Power | pwr_lim | Power_Limit | An enforced ceiling on power usage or delivery, set by controls, policies, or protection mechanisms. This is often set AFTER a derating factor has been applied | Rack PDU, Server PSU | Number | Variable Number | Power | PIT(2) | Intensive | Standalone | [13 empty] | Y | Y | Y | Y |  |  | Y |  | Y |  | Y | [14 empty] | Y | Y | Y |  | Y | Y | Y | Y |  |  | Y | Y |  | Y | Y |  | Y | [6 empty] | Y
Breaker_CurrentLimit | Reference | Power | brk_curlim | Breaker_CurrentLimit | The maximum allowable current (Amps) that a breaker is permitted to carry or interrupt, as enforced by its thermal and magnetic trip mechanisms | Switchgear, PDU/ RPP, Rack PDU | Number | Variable Number | Electrocal Current | PIT(2) | Intensive | Standalone | [38 empty] | Y |  | Y |  | Y | Y | Y | Y |  |  | Y | Y
Breaker_PowerLimit | Reference | Power | brk_pwrlim | Breaker_PowerLimit | The maximum electrical power (Watts or kW) that may pass through the breaker, derived from the current limit and operating voltage. Breaker_PowerLimit=Breaker_CurrentLimit×Nominal_Voltage×Power_Factor | Switchgear, PDU/ RPP, Rack PDU | Number | Variable Number | Power | PIT(2) | Intensive | Standalone | [38 empty] | Y |  | Y |  | Y | Y | Y | Y |  |  | Y | Y
Breaker_PowerLimit | Reference | Power | brk_pwrlim | Breaker_PowerLimit.Inherited | A power limit imposed from an upstream element (panel, PDU, feeder, UPS, or facility policy) that constrains the breaker regardless of its own physical rating. | Rack | Number | Variable Number | Power | PIT(2) | Intensive | Standalone | [13 empty] | Y | Y | Y | Y |  | Y | Y |  | Y |  | Y |  |  | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y |  | Y | Y | Y | Y | Y | Y | Y | Y | Y |  | Y | Y |  | Y | [6 empty] | Y
Power_Derating_Factor | Reference | Power | pwr_derate_fac | Power_Derating_Factor | A dimensionless multiplier (0–1) applied to rated electrical capacity to account for non-reference operating conditions and reliability requirements. | Rack, Server, Switchgear, PDU/ RPP, Rack PDU | Number | Variable Number | Ratio | PIT(2) | Intensive | Standalone | [38 empty] | Y |  | Y |  | Y | Y | Y | Y |  |  | Y | Y
Effective_Power_Limit | Reference | Power | pwr_lim_eff | Effective_Power_Limit | The final enforceable power ceiling after accounting for all applicable constraints, including breaker physics, inherited limits, and derating. | Rack, Server, Switchgear, PDU/ RPP, Rack PDU | Number | Variable Number | Power | PIT(2) | Intensive | Standalone | [13 empty] | Y | Y | Y | Y |  | Y | Y |  | Y |  | Y | [14 empty] | Y | Y | Y |  | Y | Y | Y | Y |  |  | Y | Y | Y | Y | Y |  | Y | [6 empty] | Y
Power_Headroom | Metric | Power | pwr_hdr | Power_Headroom |  | Rack, Server | Number | Variable Number | Power | PIT(2) | Intensive | Standalone | [14 empty] | Y | Y |  |  | Y | Y |  | Y |  | Y | [19 empty] | Y | Y |  |  |  |  | Y
Power_Headroom | Metric | Power | pwr_hdr | Power_Headroom.MIN(30s) | Used for racks and serversa, affecting job placement decisions | Rack, Server | Number | Variable Number | Power | PIT(2) | Intensive | Standalone |  | 5s | 30s | [11 empty] | Y | Y
Power_Headroom | Metric | Power |  | Power_Headroom.MIN(120s) | used for zones and PDUs, could affect job placement decisions if close to limit |  | Number | Variable Number | Power | PIT(2) | Intensive | Standalone |  | 60s | 120s | [20 empty] | Y | [19 empty] | Y | Y
Power_Headroom | Metric | Power |  | Power_Headroom.MIN(5m) | for UPS. useful to watching if operating near limit |  | Number | Variable Number | Power | PIT(2) | Intensive | Standalone |  | 60s | 5m | [46 empty] | Y
Power_Headroom | Metric | Power |  | Power_Headroom.AVG(5m) | For reporting purposes at room, floor, facility levels |  | Number | Variable Number | Power | PIT(2) | Intensive | Standalone |  | 5m | 5m | [15 empty] | Y | Y |  | Y
Power_Headroom | Metric | Power |  | Power_Headroom.P95(5m) | For reporting purposes at room, floor, facility levels |  | Number | Variable Number | Power | PIT(2) | Intensive | Standalone |  | 5m | 5m | [15 empty] | Y | Y |  | Y
Relative_Power_Headroom | Metric | Power | pwr_hdr_rel | Relative_Power_Headroom |  | Rack, Server | Number | Variable Number | Ratio | PIT(2) | Intensive | Standalone
Relative_Power_Headroom | Metric | Power | pwr_hdr_rel | Relative_Power_Headroom.MIN(30s) | Used for racks and servers, affecting job placement decisions | Rack, Server | Number | Variable Number | Ratio | PIT(2) | Intensive | Standalone |  | 5s | 30s | [11 empty] | Y | Y
Relative_Power_Headroom | Metric | Power |  | Relative_Power_Headroom.MIN(120s) | used for zones and PDUs, could affect job placement decisions if close to limit |  | Number | Variable Number | Ratio | PIT(2) | Intensive | Standalone |  | 60s | 120s | [40 empty] | Y | Y
Relative_Power_Headroom | Metric | Power |  | Relative_Power_Headroom.MIN(5m) | for UPS. useful to watching if operating near limit |  | Number | Variable Number | Ratio | PIT(2) | Intensive | Standalone |  | 60s | 5m | [46 empty] | Y
Relative_Power_Headroom | Metric | Power |  | Relative_Power_Headroom.AVG(5m) | For reporting purposes at room, floor, facility levels |  | Number | Variable Number | Ratio | PIT(2) | Intensive | Standalone |  | 5m | 5m | [15 empty] | Y | Y |  | Y
Relative_Power_Headroom | Metric | Power |  | Relative_Power_Headroom.P95(5m) | For reporting purposes at room, floor, facility levels |  | Number | Variable Number | Ratio | PIT(2) | Intensive | Standalone |  | 5m | 5m | [15 empty] | Y | Y |  | Y
Power_RampRate | Metric | Power | pwr_rr | Power_RampRate.60s | Used for rack and servers, reflecting local radpid changes | Rack | Number | Variable Number | Power per Time | PIT(2) | Intensive | Standalone |  | 5s | 60s | [11 empty] | Y | Y
Power_RampRate | Metric | Power | pwr_rr | Power_RampRate.120s | Used for rack and servers, reflecting local radpid changes | Rack | Number | Variable Number | Power per Time | PIT(2) | Intensive | Standalone |  | 5s | 120s | [11 empty] | Y | Y
Power_RampRate | Metric | Power |  | Power_RampRate.5m | for mid-level structures like UPS, Fabric, Pod, and for assessing thermal impacts at zone/ loop levels |  | Number | Variable Number | Power per Time | PIT(2) | Intensive | Standalone |  | 60s | 5m | [20 empty] | Y | [8 empty] | Y |  |  |  | Y | [6 empty] | Y | Y | [9 empty] | Y | [6 empty] | Y
Power_RampRate | Metric | Power |  | Power_RampRate.10m | for mid-level structures like UPS, Fabric, Pod, and for assessing thermal impacts at zone/ loop levels |  | Number | Variable Number | Power per Time | PIT(2) | Intensive | Standalone |  | 60s | 10m | [20 empty] | Y | [8 empty] | Y |  |  |  | Y | [6 empty] | Y | Y | [9 empty] | Y | [6 empty] | Y
Power_RampRate | Metric | Power |  | Power_RampRate.15m | For reporting purposes at room, floor, facility levels |  | Number | Variable Number | Power per Time | PIT(2) | Intensive | Standalone |  | 5m | 15m | [15 empty] | Y | Y |  | Y | [27 empty] | Y
Norm_Power_Increase | Metric | Power | pwr_inc_norm | Norm_Power_Increase |  | Rack | Number | Variable Number | Ratio | PIT(2) | Intensive | Standalone
Norm_Power_IncRate | Metric | Power | pwr_incr_norm | Norm_Power_IncRate |  | Rack | Number | Variable Number | Ratio per Time | PIT(2) | Intensive | Standalone
Power_JumpRating | Metric | Power | pwr_jpr | Power_JumpRating |  | Rack | Text | Variable Text |  |  | Intensive | Standalone
Power_SteepJump_Count | Metric | Power | pwr_sj_cnt | Power_SteepJump_Count.60s | for racks and servers | Rack | Number | Variable Number | Count | Interval | Extensive | Standalone |  | 5s | 60s | [11 empty] | Y | Y
Power_SteepJump_Count | Metric | Power | pwr_sj_cnt | Power_SteepJump_Count.5m | both rack, server, and zone, PDU, fabric domain, pod level monitoring | Rack | Number | Variable Number | Count | Interval | Extensive | Standalone |  | 5s | 5m | [11 empty] | Y | Y | [7 empty] | Y | [19 empty] | Y | Y | [9 empty] | Y | [6 empty] | Y
Power_SteepJump_Count | Metric | Power |  | Power_SteepJump_Count.15m | zone, PDU, fabric, Pod monitoring, and reporting at room or facility levels |  | Number | Variable Number | Count | Interval | Intensive | Standalone |  | 5m | 15m | [20 empty] | Y | [19 empty] | Y | Y | [9 empty] | Y | [6 empty] | Y
Power_Burstiness | Metric | Power | pwr_burst | Power_Burstiness.60s | for racks and servers | Rack | Number | Variable Number | Ratio per Time | PIT(2) | Intensive | Standalone |  | 5s | 60s | [11 empty] | Y | Y
Power_Burstiness | Metric | Power | pwr_burst | Power_Burstiness.5m | both rack, server, and zone, PDU, fabric domain, pod level monitoring | Rack | Number | Variable Number | Ratio per Time | PIT(2) | Intensive | Standalone |  | 5s | 5m | [11 empty] | Y | Y | [7 empty] | Y | [19 empty] | Y | Y | [9 empty] | Y | [6 empty] | Y
Power_Burstiness | Metric | Power |  | Power_Burstiness.15m | zone, PDU, fabric, Pod monitoring, and reporting at room or facility levels |  | Number | Variable Number | Ratio per Time | PIT(2) | Intensive | Standalone |  | 5m | 15m | [20 empty] | Y | [19 empty] | Y | Y | [9 empty] | Y | [6 empty] | Y
Power_Excess | Metric | Power | pwr_exc | Power_Excess |  | Rack, Server | Number | Variable Number | Ratio | PIT(2) | Intensive | Standalone
Power_Overlimit_Event | Event | Power |  | Power_Overlimit_Event |  | Rack, Server | Date Time | Variable Date Time |  |  |  | Standalone |  | NA | NA | [11 empty] | Y | Y |  |  | Y | Y |  | Y |  | Y | [19 empty] | Y | Y |  |  |  |  | Y |  |  |  |  | Y | [6 empty] | Y
Power_Overlimit_Time | Metric | Power | pwr_ovrlim_time | Power_Overlimit_Time.60s |  | Rack | Number | Variable Number | Time | Interval | Intensive | Standalone |  | 5s/60s | 60s | [11 empty] | Y | Y |  |  | Y | Y |  | Y |  | Y | [19 empty] | Y | Y |  |  |  |  | Y |  |  |  |  | Y | [6 empty] | Y
Power_Overlimit_Time | Metric | Power | pwr_ovrlim_time | Power_Overlimit_Time.15m |  | Rack | Number | Variable Number | Time | Interval | Intensive | Standalone |  | 5s/60s | 15m | [11 empty] | Y | Y |  |  | Y | Y |  | Y |  | Y | [19 empty] | Y | Y |  |  |  |  | Y |  |  |  |  | Y | [6 empty] | Y
Relative_Power_Overshoot | Metric | Power | pwr_os_rel | Relative_Power_Overshoot.60s |  | Rack | Number | Variable Number | Ratio times Time | Interval | Intensive | Standalone |  | 5s/60s | 60s | [11 empty] | Y | Y |  |  | Y | Y |  | Y |  | Y | [19 empty] | Y | Y |  |  |  |  | Y |  |  |  |  | Y | [6 empty] | Y
Relative_Power_Overshoot | Metric | Power | pwr_os_rel | Relative_Power_Overshoot.15m |  | Rack | Number | Variable Number | Ratio times Time | Interval | Intensive | Standalone |  | 5s/60s | 15m | [11 empty] | Y | Y |  |  | Y | Y |  | Y |  | Y | [19 empty] | Y | Y |  |  |  |  | Y |  |  |  |  | Y | [6 empty] | Y
Power_Overshoot | Metric | Power | pwr_os | Power_Overshoot.60s |  | Rack | Number | Variable Number | Power times Time | Interval | Intensive | Standalone |  | 5s/60s | 60s | [11 empty] | Y | Y |  |  | Y | Y |  | Y |  | Y | [19 empty] | Y | Y |  |  |  |  | Y |  |  |  |  | Y | [6 empty] | Y
Power_Overshoot | Metric | Power | pwr_os | Power_Overshoot.15m |  | Rack | Number | Variable Number | Power times Time | Interval | Intensive | Standalone |  | 5s/60s | 15m | [11 empty] | Y | Y |  |  | Y | Y |  | Y |  | Y | [19 empty] | Y | Y |  |  |  |  | Y |  |  |  |  | Y | [6 empty] | Y
Temperature | Input | Thermal | temp | Temperature.InletTop |  | Rack | Number | Variable Number | Temperature | PIT(2) | Intensive | Standalone | [14 empty] | Y
Temperature | Input | Thermal | temp | Temperature.InletMid |  | Rack | Number | Variable Number | Temperature | PIT(2) | Intensive | Standalone | [14 empty] | Y
Temperature | Input | Thermal | temp | Temperature.InletBottom |  | Rack | Number | Variable Number | Temperature | PIT(2) | Intensive | Standalone | [14 empty] | Y
Temperature | Input | Thermal | tmp_op | Temperature.Inlet | tempereture of air entering IT system, for racks, servers, and air zones | Rack, Server | Number | Variable Number | Temperature | PIT(2) | Intensive | Standalone | [14 empty] | Y | Y | [16 empty] | Y
Temperature | Input | Thermal |  | Temperature.ambient | temperature or average temperature in larger facility areas |  | Number | Variable Number | Temperature | PIT(2) | Intensive | Standalone | [18 empty] | Y | Y |  | Y
Thermal_Limit | Reference | Thermal | thm_lim | Thermal_Limit |  | Rack, Server | Number | Variable Number | Temperature | PIT(2) | Intensive | Standalone | [14 empty] | Y | Y | [16 empty] | Y
Thermal_Headroom | Metric | Thermal | thm_hdr | Thermal_Headroom | thermal headroom is for racks, servers, and air zones | Rack, Server | Number | Variable Number | Temperature | PIT(2) | Intensive | Standalone |  | 30s | [12 empty] | Y | Y | [16 empty] | Y
Thermal_Headroom | Metric | Thermal | thm_hdr | Thermal_Headroom.MIN(2m) | thermal headroom is for racks, servers, and air zones | Rack, Server | Number | Variable Number | Temperature | PIT(2) | Intensive | Standalone |  | 30s | 2m | [11 empty] | Y | Y | [16 empty] | Y
Thermal_Headroom | Metric | Thermal | thm_hdr | Thermal_Headroom.MIN(5m) | thermal headroom is for racks, servers, and air zones | Rack, Server | Number | Variable Number | Temperature | PIT(2) | Intensive | Standalone |  | 30s | 5m | [11 empty] | Y | Y | [16 empty] | Y
Thermal_Headroom | Metric | Thermal | thm_hdr | Thermal_Headroom.MIN(10m) | obsolete | [8 empty] | 30s | 10m
Thermal_Headroom | Metric | Thermal | thm_hdr | Thermal_Headroom.MIN(30m) | obsolete | [8 empty] | 30s | 30m
Thermal_Coupling | Metric | Thermal | thm_cpl | Thermal_Coupling.10m |  | Rack | Number | Variable Number | Temperature per Power | PIT(2) | Intensive | Standalone |  | 60s | 10m | [11 empty] | Y
Thermal_Coupling | Metric | Thermal | thm_cpl | Thermal_Coupling.30m |  | Rack | Number | Variable Number | Temperature per Power | PIT(2) | Intensive | Standalone |  | 60s | 30m | [11 empty] | Y
Thermal_Coupling | Metric | Thermal | thm_cpl | Thermal_Coupling.24h |  | Rack | Number | Variable Number | Temperature per Power | PIT(2) | Intensive | Standalone |  | 15m | 24h | [11 empty] | Y
Local_Temp_Diff | Metric | Thermal | tmp_diff_loc | Local_Temp_Diff |  | Rack | Number | Variable Number | Temperature | PIT(2) | Intensive | Standalone | [14 empty] | Y
Local_Temp_Diff | Metric | Thermal | tmp_diff_loc | Local_Temp_Diff.MAX(2m) |  |  | Number | Variable Number | Temperature | PIT(2) | Intensive | Standalone |  | 30s | 2m | [11 empty] | Y
Local_Temp_Diff | Metric | Thermal | tmp_diff_loc | Local_Temp_Diff.MAX(5m) |  |  | Number | Variable Number | Temperature | PIT(2) | Intensive | Standalone |  | 30s | 5m | [11 empty] | Y
Local_Temp_Diff | Metric | Thermal | tmp_diff_loc | Local_Temp_Diff.MAX(10m) | obsolete | Rack | Number | Variable Number | Temperature | PIT(2) | Intensive | Standalone
Local_Temp_Diff | Metric | Thermal | tmp_diff_loc | Local_Temp_Diff.MAX(30m) | obsolete | Rack | Number | Variable Number | Temperature | PIT(2) | Intensive | Standalone
Thermal_Excess | Metric | Thermal | thm_exc | Thermal_Excess |  | Rack, Server | Number | Variable Number | Temperature | PIT(2) | Intensive | Standalone
Thermal_Overheat_Event | Event | Thermal |  | Thermal_Overheat_Event |  | Rack, Server | Date Time | Variable Date Time |  |  |  | Standalone |  | NA | NA | [11 empty] | Y | Y | [16 empty] | Y
Thermal_Overheat_Time | Metric | Thermal |  | Thermal_Overheat_Time.5m |  |  | Number | Variable Number | Time | Interval | Intensive | Standalone |  | 30s | 5m | [11 empty] | Y | Y | [16 empty] | Y
Thermal_Overheat_Time | Metric | Thermal | thm_oh_time | Thermal_Overheat_Time.10m |  | Rack, Server | Number | Variable Number | Time | Interval | Intensive | Standalone |  | 30s | 10m | [11 empty] | Y | Y | [16 empty] | Y
Thermal_Overheat_Time | Metric | Thermal | thm_oh_time | Thermal_Overheat_Time.15m | obsolete | Rack, Server | Number | Variable Number | Time | Interval | Intensive | Standalone
Temp_Overshoot | Metric | Thermal |  | Temp_Overshoot.15m |  |  | Number | Variable Number | Temperature times Time | Interval | Intensive | Standalone |  | 30s | 15m | [11 empty] | Y | Y | [16 empty] | Y
Temp_Overshoot | Metric | Thermal | tmp_os | Temp_Overshoot.30m |  | Rack, Server | Number | Variable Number | Temperature times Time | Interval | Intensive | Standalone |  | 30s | 30m | [11 empty] | Y | Y | [16 empty] | Y
Fan_Speed_Limit | Reference | Cooling | fan_spd_lim | Fan_Speed_Limit |  | Server | Number | Variable Number | Rotational Speed | PIT(2) | Intensive | Standalone | [15 empty] | Y
Fan_Speed | Input | Cooling | fan_spd | Fan_Speed |  | Server | Number | Variable Number | Rotational Speed | PIT(2) | Intensive | Standalone | [15 empty] | Y
Fan_Saturation | Metric | Cooling | fan_sat | Fan_Saturation.AVG(30s) |  | Server | Number | Variable Number | Ratio | PIT(2) | Intensive | Standalone |  | 30s | 30s | [12 empty] | Y
Liquid_SupplyTemp | Input | Cooling | liq_sup_t | Liquid_SupplyTemp |  | LiquidLoop | Number | Variable Number | Temperature | PIT(2) | Intensive | Standalone | [36 empty] | Y
Liquid_ReturnTemp | Input | Cooling | liq_ret_t | Liquid_ReturnTemp |  | Liquid Loop | Number | Variable Number | Temperature | PIT(2) | Intensive | Standalone | [36 empty] | Y
Liquid_SupplyT_Limit | Reference | Cooling | liq_sup_t_lim | Liquid_SupplyT_Limit |  | Liquid Loop | Number | Variable Number | Temperature | PIT(2) | Intensive | Standalone | [36 empty] | Y
Liquid_SupplyT_Margin | Metric | Cooling | liq_sup_t_mg | Liquid_SupplyT_Margin |  | Liquid Loop | Number | Variable Number | Temperature | PIT(2) | Intensive | Standalone |  | 30s | [34 empty] | Y
Liquid_SupplyT_Margin | Metric | Cooling | liq_sup_t_mg | Liquid_SupplyT_Margin.MIN(10m) |  | Liquid Loop | Number | Variable Number | Temperature | PIT(2) | Intensive | Standalone |  | 30s | 10m | [33 empty] | Y
Liquid_SupplyT_Margin | Metric | Cooling | liq_sup_t_mg | Liquid_SupplyT_Margin.MIN(30m) |  | Liquid Loop | Number | Variable Number | Temperature | PIT(2) | Intensive | Standalone |  | 30s | 30m | [33 empty] | Y
Liquid_ReturndT_perkW | Metric | Cooling | liq_ret_dt_kw | Liquid_ReturndT_perkW.10m |  | Liquid Loop | Number | Variable Number | Temperature per Power | PIT(2) | Intensive | Standalone |  | 30s | 10m | [33 empty] | Y
Liquid_ReturndT_perkW | Metric | Cooling | liq_ret_dt_kw | Liquid_ReturndT_perkW.30m |  | Liquid Loop | Number | Variable Number | Temperature per Power | PIT(2) | Intensive | Standalone |  | 30s | 30m | [33 empty] | Y
Pump_Speed | Input | Cooling | pump_spd | Pump_Speed.5m |  | Liquid Loop | Number | Variable Number | Rotational Speed | PIT(2) | Intensive | Standalone
Pump_Speed_Limit | Reference | Cooling | pump_spd_lim | Pump_Speed_Limit |  | Liquid Loop | Number | Variable Number | Rotational Speed | PIT(2) | Intensive | Standalone
Pump_Control_Percent | Input | Cooling | pump_ctrl_pct | Pump_Control_Percent.P(n) |  | Liquid Loop | Number | Variable Number | Ratio | PIT(2) | Intensive | Standalone | [36 empty] | Y
Pump_Saturation | Input | Cooling | pump_sat | Pump_Saturation.P(n) |  | Liquid Loop | Number | Variable Number | Ratio | PIT(2) | Intensive | Standalone | [36 empty] | Y
Pump_Saturation | Input | Cooling | pump_sat | Pump_Saturation.P(n).5m |  | Liquid Loop | Number | Variable Number | Ratio | PIT(2) | Intensive | Standalone | [36 empty] | Y
Pump_Saturation | Metric | Cooling | pump_sat | Pump_Saturation.MAX.5m |  | Liquid Loop | Number | Variable Number | Ratio | PIT(2) | Intensive | Standalone |  | 30s | 5m | [33 empty] | Y
Air_SupplyTemp | Input |  |  | Air_SupplyTemp | [40 empty] | Y
Air_ReturnTemp | Input |  |  | Air_ReturnTemp | [40 empty] | Y
Air_SupplyT_Limit | Input |  |  | Air_SupplyT_Limit | [40 empty] | Y
Air_SupplyT_Margin | Input |  |  | Air_SupplyT_Margin | [40 empty] | Y
Breaker_Headroom | Metric | Power | brk_hdr | Breaker_Headroom |  | Switchgear, PDU/ RPP, Rack PDU | Number | Variable Number | Power | PIT(2) | Intensive | Standalone | [38 empty] | Y |  | Y |  | Y |  | Y | Y |  |  | Y | Y | Y
Breaker_Headroom | Metric | Power | brk_hdr | Breaker_Headroom.MIIN(30s) | for Rack PDU | Switchgear, PDU/ RPP, Rack PDU | Number | Variable Number | Power | PIT(2) | Intensive | Standalone |  | 5s | 30s | [42 empty] | Y
Breaker_Headroom | Metric | Power |  | Breaker_Headroom.AVG(2m) | for Rack PDU, Captures sustained near-overload without being too sticky; ramps are still relevant. |  | Number | Variable Number | Power | PIT(2) | Intensive | Standalone |  | 5s | 2m | [42 empty] | Y
Breaker_Headroom | Metric | Power |  | Breaker_Headroom.AVG(5m) | for PDU, Good default for feeder protection behavior and thermal inertia. for BESS |  | Number | Variable Number | Power | PIT(2) | Intensive | Standalone |  | 5s | 5m | [35 empty] | Y |  | Y |  |  |  | Y
Breaker_Headroom | Metric | Power |  | Breaker_Headroom.AVG(10m) | for mechanical power panel, UPS, and switch gear |  | Number | Variable Number | Power | PIT(2) | Intensive | Standalone |  | 5s | 10m | [39 empty] | Y | [5 empty] | Y | Y
Min_Headroom_UpstreamBreaker | Metric | Power | min_hdr_upbrk | Min_Headroom_UpstreamBreaker.FeedA.30s |  | Rack | Number | Variable Number | Power | PIT(2) | Intensive | Standalone
Min_Headroom_UpstreamBreaker | Metric | Power | min_hdr_upbrk | Min_Headroom_UpstreamBreaker.FeedB.30s |  | Rack | Number | Variable Number | Power | PIT(2) | Intensive | Standalone
MinPower_Headroom_UpstreamBreaker | Metric | Power | pwr_hdr_min_upbrk | Min_Headroom_UpstreamBreaker.30s |  | Rack | Number | Variable Number | Power | PIT(2) | Intensive | Standalone |  | 5s | 30s | [11 empty] | Y | Y | [7 empty] | Y | [30 empty] | Y | [6 empty] | Y
Power_Peak_Probability | Metric | Power | pwr_peak_prob | Power_Peak_Probability.1m |  | Rack, Server | Number | Variable Number | Ratio | PIT(2) | Intensive | Standalone |  | 5s | 1m | [11 empty] | Y | Y | [7 empty] | Y | [30 empty] | Y | [6 empty] | Y
Power_Peak_Probability | Metric | Power | pwr_peak_prob | Power_Peak_Probability.5m |  | Rack, Server | Number | Variable Number | Ratio | PIT(2) | Intensive | Stand alone |  | 5s | 5m | [11 empty] | Y | Y | [7 empty] | Y | [30 empty] | Y | [6 empty] | Y
Power_Usage_Std | Metric | Power |  | Power_Usage_Std.2m |  | Server | Number | Variable Number | Dimensionless | PIT(2) | Intensive | Stand alone |  | 5s | 2m
Power_Headroom_Factor | Metric | Power | pwr_hdr_fac | Power_Headroom_Factor |  | Rack, Server | Number | Variable Number | Dimensionless | PIT(2) | Intensive | Stand alone | [14 empty] | Y | Y
Power_RampRate_Factor | Metric | Power | pwr_rr_fac | Power_RampRate_Factor |  | Rack | Number | Variable Number | Dimensionless | PIT(2) | Intensive | Stand alone | [14 empty] | Y
Power_Burstiness_Factor | Metric | Power | pwr_burst_fac | Power_Burstiness_Factor |  | Rack | Number | Variable Number | Dimensionless | PIT(2) | Intensive | Stand alone | [14 empty] | Y
Power_PeakRisk_Factor | Metric | Power | pwr_peakrisk_fac | Power_PeakRisk_Factor |  | Rack | Number | Variable Number | Dimensionless | PIT(2) | Intensive | Stand alone | [14 empty] | Y | Y
Power_Overlimit_Factor | Metric | Power | pwr_overlim_fac | Power_Overlimit_Factor |  | Rack, Server | Number | Variable Number | Dimensionless | PIT(2) | Intensive | Stand alone | [14 empty] | Y | Y
Thermal_Headroom_Factor | Metric | Thermal | thm_hdr_fac | Thermal_Headroom_Factor |  | Rack, Server | Number | Variable Number | Dimensionless | PIT(2) | Intensive | Stand alone | [14 empty] | Y | Y
Thermal_Hotspot_Factor | Metric | Thermal | thm_hspt_fac | Thermal_Hotspot_Factor |  | Rack | Number | Variable Number | Dimensionless | PIT(2) | Intensive | Stand alone | [14 empty] | Y
Thermal_Overheat_Factor | Metric | Thermal | thm_oh_fac | Thermal_Overheat_Factor |  | Rack, Server | Number | Variable Number | Dimensionless | PIT(2) | Intensive | Stand alone | [14 empty] | Y | Y
Thermal_Coupling_Factor | Metric | Thermal | thm_cpl_fac | Thermal_Coupling_Factor |  | Rack | Number | Variable Number | Dimensionless | PIT(2) | Intensive | Stand alone | [14 empty] | Y
Cooling_Efficiency_Factor | Metric | Cooling | cool_eff_fac | Cooling_Efficiency_Factor |  | Rack | Number | Variable Number | Dimensionless | PIT(2) | Intensive | Stand alone | [14 empty] | Y
Fan_Saturation_Factor | Metric | Cooling | fan_sac_fac | Fan_Saturation_Factor |  | Server | Number | Variable Number | Dimensionless | PIT(2) | Intensive | Stand alone | [15 empty] | Y
Liquid_SupplyT_Margin_Factor | Metric | Cooling | liq_sup_t_mg_fac | Liquid_SupplyT_Margin_Factor |  | Liquid Loop | Number | Variable Number | Dimensionless | PIT(2) | Intensive | Stand alone | [36 empty] | Y
Liquid_ReturndT_perkW_Factor | Metric | Cooling | liq_ret_dt_kw_fac | Liquid_ReturndT_perkW_Factor |  | Liquid Loop | Number | Variable Number | Dimensionless | PIT(2) | Intensive | Stand alone | [36 empty] | Y
Pump_Saturation_Factor | Metric | Cooling | pump_sac_fac | Pump_Saturation_Factor |  | Liquid Loop | Number | Variable Number | Dimensionless | PIT(2) | Intensive | Stand alone | [36 empty] | Y
UpstreamBreaker_Headroom_Factor | Metric | Power | pwr_hdr_up_brk_fac | UpstreamBreaker_Headroom_Factor |  | Rack | Number | Variable Number | Dimensionless | PIT(2) | Intensive | Stand alone | [14 empty] | Y
Batchability_PowerProxy_Factor | Metric | Compute | batch_pwrproxy_fac | Batchability_PowerProxy_Factor |  | Server | Number | Variable Number | Dimensionless | PIT(2) | Intensive | Stand alone | [52 empty] | Y
Power_Headroom_wt | Reference | Power | pwr_hdr_wt | Power_Headroom_wt |  | Rack, Server | Number | Variable Number | Dimensionless | PIT(2) | Intensive | Stand alone | [14 empty] | Y | Y
Power_RampRate_wt | Reference | Power | pwr_rr_wt | Power_RampRate_wt |  | Rack | Number | Variable Number | Dimensionless | PIT(2) | Intensive | Stand alone | [14 empty] | Y
Power_Burstiness_wt | Reference | Power | pwr_burst_wt | Power_Burstiness_wt |  | Rack | Number | Variable Number | Dimensionless | PIT(2) | Intensive | Stand alone | [14 empty] | Y
Power_PeakRisk_wt | Reference | Power | pwr_peakrisk_wt | Power_PeakRisk_wt |  | Rack | Number | Variable Number | Dimensionless | PIT(2) | Intensive | Stand alone | [14 empty] | Y | Y
Power_Overlimit_wt | Reference | Power | pwr_overlim_wt | Power_Overlimit_wt |  | Rack, Server | Number | Variable Number | Dimensionless | PIT(2) | Intensive | Stand alone | [14 empty] | Y | Y
Thermal_Headroom_wt | Reference | Thermal | thm_hdr_wt | Thermal_Headroom_wt |  | Rack, Server | Number | Variable Number | Dimensionless | PIT(2) | Intensive | Stand alone | [14 empty] | Y | Y
Thermal_Hotspot_wt | Reference | Thermal | thm_hspt_wt | Thermal_Hotspot_wt |  | Rack | Number | Variable Number | Dimensionless | PIT(2) | Intensive | Stand alone | [14 empty] | Y
Thermal_Overheat_wt | Reference | Thermal | thm_oh_wt | Thermal_Overheat_wt |  | Rack, Server | Number | Variable Number | Dimensionless | PIT(2) | Intensive | Stand alone | [14 empty] | Y | Y
Thermal_Coupling_wt | Reference | Thermal | thm_cpl_wt | Thermal_Coupling_wt |  | Rack | Number | Variable Number | Dimensionless | PIT(2) | Intensive | Stand alone | [14 empty] | Y
Cooling_Efficiency_wt | Reference | Cooling | cool_eff_wt | Cooling_Efficiencty_wt |  | Rack | Number | Variable Number | Dimensionless | PIT(2) | Intensive | Stand alone | [14 empty] | Y
Fan_Saturation_wt | Reference | Cooling | fan_sac_wt | Fan_Saturation_wt |  | Server | Number | Variable Number | Dimensionless | PIT(2) | Intensive | Stand alone | [15 empty] | Y
Liquid_SupplyT_Margin_wt | Reference | Cooling | liq_sup_t_mg_wt | Liquid_SupplyT_Margin_wt |  | Liquid Loop | Number | Variable Number | Dimensionless | PIT(2) | Intensive | Stand alone | [36 empty] | Y
Liquid_ReturndT_perkW_wt | Reference | Cooling | liq_ret_dt_kw_wt | Liquid_ReturndT_perkW_wt |  | Liquid Loop | Number | Variable Number | Dimensionless | PIT(2) | Intensive | Stand alone | [36 empty] | Y
Pump_Saturation_wt | Reference | Cooling | pump_sac_wt | Pump_Saturation_wt |  | Liquid Loop | Number | Variable Number | Dimensionless | PIT(2) | Intensive | Stand alone | [36 empty] | Y
UpstreamBreaker_Headroom_wt | Reference | Power | pwr_hdr_up_brk_wt | UpstreamBreaker_Headroom_wt |  | Rack | Number | Variable Number | Dimensionless | PIT(2) | Intensive | Stand alone | [14 empty] | Y
Batchability_PowerProxy_wt | Reference | Compute | batch_pwrproxy_wt | Batchability_PowerProxy_wt |  | Compute Node | Number | Variable Number | Dimensionless | PIT(2) | Intensive | Stand alone | [52 empty] | Y
Power_Fitness_Index | Metric | Power | pwr_fit_idx | Power_Fitness_Index |  | Rack, Server | Number | Variable Number | Dimensionless | PIT(2) | Intensive | Stand alone | [14 empty] | Y | Y
Thermal_Fitness_Index | Metric | Thermal | thm_fit_idx | Thermal_Fitness_Index |  | Rack, Server | Number | Variable Number | Dimensionless | PIT(2) | Intensive | Stand alone | [14 empty] | Y | Y
Cooling_Efficiency_Index | Metric | Cooling | cool_fit_idx | Cooling_Efficiency_Index |  | Rack | Number | Variable Number | Dimensionless | PIT(2) | Intensive | Stand alone | [14 empty] | Y
LiquidCooling_Fitness_Index | Metric | Cooling | liqcool_fit_idx | LiquidCooling_Fitness_Index |  | Liquid Loop | Number | Variable Number | Dimensionless | PIT(2) | Intensive | Stand alone | [36 empty] | Y
Upstream_PowerRisk_Index | Metric | Power | pwr_risk_up_idx | Upstream_PowerRisk_Index |  | Rack | Number | Variable Number | Dimensionless | PIT(2) | Intensive | Stand alone | [14 empty] | Y
Batching_Fitness_Index | Metric | Compute | batch_fit_idx | Batching_Fitness_Index |  | Compute Node | Number | Variable Number | Dimensionless | PIT(2) | Intensive | Stand alone | [52 empty] | Y
Power_Fitness_Index_wt | Reference | Power | pwr_fit_wt | Power_Fitness_Index_wt |  | Rack, Server | Number | Variable Number | Dimensionless | PIT(2) | Intensive | Stand alone | [14 empty] | Y | Y
Thermal_Fitness_Index_wt | Reference | Thermal | thm_fit_wt | Thermal_Fitness_Index_wt |  | Rack, Server | Number | Variable Number | Dimensionless | PIT(2) | Intensive | Stand alone | [14 empty] | Y | Y
Cooling_Efficiency_Index_wt | Reference | Cooling | cool_fit_wt | Cooling_Efficiency_Index_wt |  | Rack | Number | Variable Number | Dimensionless | PIT(2) | Intensive | Stand alone | [14 empty] | Y
LiquidCooling_Fitness_Index_wt | Reference | Cooling | liqcool_fit_wt | LiquidCooling_Fitness_Index_wt |  | Liquid Loop | Number | Variable Number | Dimensionless | PIT(2) | Intensive | Stand alone | [36 empty] | Y
Upstream_PowerRisk_Index_wt | Reference | Power | pwr_risk_up_wt | Upstream_PowerRisk_Index_wt |  | Rack | Number | Variable Number | Dimensionless | PIT(2) | Intensive | Stand alone | [14 empty] | Y
Batching_Fitness_Index_wt | Reference | Compute | batch_fit_wt | Batching_Fitness_Index_wt |  | Compute Node | Number | Variable Number | Dimensionless | PIT(2) | Intensive | Stand alone | [52 empty] | Y
Node_Fitness_Index | Metric | Composite |  | Node_Fitness_Index |  | Compute Node | Number | Variable Number | Dimensionless | PIT(2) | Intensive | Stand alone |  | 5s | last available input | [49 empty] | Y
GPU_Count | Reference |  |  | GPU_Count | [22 empty] | Y | Y | [36 empty] | Y |  | Y | [6 empty] | Y
GPU_Utilization | Metric |  |  | GPU_Utilization | [22 empty] | Y | Y | [36 empty] | Y |  | Y | [6 empty] | Y
PUE | Metric |  |  | PUE | [27 empty] | Y
| Reference |  |  | Rack_Circuit_Capacity_(rated) | The rack capacity limit imposed by the branch circuit breaker from RPP, before derating | [21 empty] | Y
| Reference |  |  | Rack_Circuit_Capacity_(design) | The rack capacity limit imposed by the branch circuit breaker from RPP, after applying a derating factor, often 80% |  | Number | Constant Number | Power | PIT(2) | Extensive | Standard Rollup | [5 empty] | Y | [8 empty] | Y |  |  |  | Y | Y |  | Y |  | Y | Y | [38 empty] | Y | Y | Y | Y | Y | Y | Y | Y
| Input |  |  | Allocated_ITLoad | The kW load that is allocated to racks |  | Number | Constant Number | Power | PIT(2) | Extensive | Standard Rollup | [5 empty] | Y |  | Y | Y | [5 empty] | Y |  |  |  | Y | Y |  | Y |  | Y | Y |  | Y | [5 empty] | Y | Y | Y |  | Y |  | Y |  | Y |  |  | Y | Y |  |  |  | Y | Y | Y | [15 empty] | Y | Y | Y | Y | Y
| Input |  |  | TheorMax_ITLoad | The sum of peak load for each device in the rack is hte maximum theoretical IT load |  | Number | Constant Number | Power | PIT(2) | Extensive | Standard Rollup | [5 empty] | Y |  | Y | Y | [5 empty] | Y |  |  |  | Y | Y |  | Y |  | Y | Y |  | Y | [5 empty] | Y | Y | Y |  | Y |  | Y |  | Y |  |  | Y | Y |  |  |  | Y | Y | Y | [15 empty] | Y | Y | Y | Y | Y
| Reference |  |  | Rack_AirCool_Fraction | the fraction of heat desgined to be removed by air |  | Number | Constant Number | Ratio | PIT(2) | Intensive | Stand alone
| Reference |  |  | Rack_LiquidCool_Fraction | the fraction of heat desgined to be removed by liquid cooling |  | Number | Constant Number | Ratio | PIT(2) | Intensive | Stand alone
| Metric |  |  | Allocated_AirCool_Load |  |  | Number | Constant Number | Power | PIT(2) | Extensive | Standard Rollup | [7 empty] | Y |  |  |  | Y | Y |  | Y | [17 empty] | Y | Y | Y |  | Y | [26 empty] | Y | Y | Y | Y | Y | Y | Y | Y
| Metric |  |  | Allocated_LiquidCool_Load |  |  | Number | Constant Number | Power | PIT(2) | Extensive | Standard Rollup | [7 empty] | Y |  |  |  | Y | Y |  | Y | [17 empty] | Y | Y | Y |  | Y | [26 empty] | Y | Y | Y | Y | Y | Y | Y | Y
| Metric |  |  | TheorMax_AirCool_Load |  |  | Number | Constant Number | Power | PIT(2) | Extensive | Standard Rollup | [7 empty] | Y |  |  |  | Y | Y |  | Y | [17 empty] | Y | Y | Y |  | Y | [26 empty] | Y | Y | Y | Y | Y | Y | Y | Y
| Metric |  |  | TheorMax_LiquidCool_Load |  |  | Number | Constant Number | Power | PIT(2) | Extensive | Standard Rollup | [7 empty] | Y |  |  |  | Y | Y |  | Y | [17 empty] | Y | Y | Y |  | Y | [26 empty] | Y | Y | Y | Y | Y | Y | Y | Y
| Metric |  |  | Local_Capacity_Margin | local to each capacity node, calculated by the Capacity cap - Allocated IT Load |  | Number | Constant Number | Power | PIT(2) | Extensive | Stand alone | [14 empty] | Y | [17 empty] | Y | Y | Y |  | Y |  |  |  | Y |  |  | Y | [5 empty] | Y
| Metric |  |  | Local_Capacity_Margin% |  |  | Number | Constant Number | Ratio | PIT(2) | Intensive | Stand alone | [14 empty] | Y | [17 empty] | Y | Y | Y |  | Y |  |  |  | Y |  |  | Y | [5 empty] | Y
| Metric |  |  | Device_Capacity_Margin | specific to the device, calculated by the device's design capacith - allocated It load |  | Number | Constant Number | Power | PIT(2) | Extensive | Stand alone | [43 empty] | Y | Y
| Metric |  |  | Device_Capacity_Margin% |  |  | Number | Constant Number | Ratio | PIT(2) | Intensive | Stand alone | [43 empty] | Y | Y
| Metric |  |  | Upstream_Capacity_Margin |  |  | Number | Constant Number | Power | PIT(2) | Extensive | Stand alone | [14 empty] | Y | Y | Y | Y | [14 empty] | Y | Y |  | Y | Y | Y | [5 empty] | Y | Y |  |  |  |  | Y
| Metric |  |  | Upstream_Capacity_Margin% |  |  | Number | Constant Number | Ratio | PIT(2) | Intensive | Stand alone | [14 empty] | Y | Y | Y | Y | [14 empty] | Y | Y |  | Y | Y | Y | [5 empty] | Y | Y |  |  |  |  | Y
| Metric |  |  | Rack_Count |  |  | Number | Constant Number | Count | PIT(2) | Extensive | Standard Rollup | [5 empty] | Y |  | Y | Y | [5 empty] | Y |  |  |  | Y | Y |  | Y |  | Y | Y |  | Y | [5 empty] | Y | Y | Y |  | Y |  | Y |  | Y |  |  | Y | Y |  |  |  | Y | Y | Y | [15 empty] | Y | Y | Y | Y | Y
| Reference |  |  | Rated_Cooling_Capacity |  |  | Number | Constant Number | Power | PIT(2) | Extensive | Stand alone | [26 empty] | Y | Y
| Reference |  |  | Pump_Capacity |  |  | Number | Constant Number | Flow Rate | PIT(2) | Intensive | Stand alone | [27 empty] | Y
| Reference |  |  | RPP_Panel_Capacity_(rated) |  |  | Number | Constant Number | Power | PIT(2) | Extensive | Stand alone | [44 empty] | Y
| Reference |  |  | RPP_Panel_Capacity_(design) | RPP panel capacity (rated) after applying derating |  | Number | Constant Number | Power | PIT(2) | Extensive | Stand alone | [44 empty] | Y | [18 empty] | Y | Y | Y | Y | Y | Y | Y | Y
| Reference |  |  | RPP_BreakerPole_Capacity |  |  | Number | Constant Number | Count | PIT(2) | Extensive | Stand alone | [44 empty] | Y
| Reference |  |  | AirZone_Cooling_Capacity |  |  | Number | Constant Number | Power | PIT(2) | Extensive | Stand alone | [63 empty] | Y | Y | Y | Y | Y | Y | Y | Y
| Reference |  |  | Maximum_Air_Flow |  |  | Number | Constant Number | Flow Rate | PIT(2) | Intensive | Stand alone | [26 empty] | Y | [5 empty] | Y
| Reference |  |  | Rack_Inlet_Setpoint | arget temperature at the server inlet used for control and alarms. |  | Number | Constant Number | Temperature | PIT(2) | Intensive | Stand alone | [32 empty] | Y
| Reference |  |  | ColdAisle_Supply_Temp | emperature of air delivered into the cold aisle from the cooling system. |  | Number | Constant Number | Temperature | PIT(2) | Intensive | Stand alone | [32 empty] | Y
| Reference |  |  | Rack_DeltaT_(design) | design temperature rise across the rack: inlet → exhaust. |  | Number | Constant Number | Temperature | PIT(2) | Intensive | Stand alone | [32 empty] | Y
| Reference |  |  | LL_Cooling_Capacity |  |  | Number | Constant Number | Power | PIT(2) | Extensive | Stand alone
| Reference |  |  | Loop_Supply_Setpoint | coolant temperature delivered from the CDU to the rack liquid loop. |  | Number | Constant Number | Temperature | PIT(2) | Intensive | Stand alone | [36 empty] | Y
| Reference |  |  | Loop_DeltaT_(design) | return minus supply |  | Number | Constant Number | Temperature | PIT(2) | Intensive | Stand alone | [36 empty] | Y
| Reference |  |  | RPDU_Transformer_Rating | Nameplate capacity of the RPDU transformer (kVA or kW). |  | Number | Constant Number | Power | PIT(2) | Extensive | Stand alone | [43 empty] | Y
| Reference |  |  | RPDU_Design_Capacity | Transformer rating × engineering derating (e.g., thermal margin, continuous load assumptions). |  | Number | Constant Number | Power | PIT(2) | Extensive | Stand alone | [43 empty] | Y
| Reference |  |  | RPDU_Operational_Cap | Planning envelope used by operators to control deployment. Often lower than design capacity to preserve redundancy or growth margin. |  | Number | Constant Number | Power | PIT(2) | Extensive | Stand alone | [43 empty] | Y | [19 empty] | Y | Y | Y | Y | Y | Y | Y | Y
| Reference |  |  | UPS_Rated_Capacity | Nameplate maximum output of the UPS system/module configuration. This is the hard equipment rating. |  | Number | Constant Number | Power | PIT(2) | Extensive | Stand alone | [49 empty] | Y
| Reference |  |  | UPS_Design_Capacity | Rated capacity after any engineering derating or design assumptions. In some facilities this may equal the rated capacity, but in your model it is the local device-side usable capacity. |  | Number | Constant Number | Power | PIT(2) | Extensive | Stand alone | [49 empty] | Y
| Reference |  |  | UPS_Operational_Cap | The lower planning envelope operators use for deployment, redundancy, and growth margin. |  | Number | Constant Number | Power | PIT(2) | Extensive | Stand alone | [49 empty] | Y | [13 empty] | Y | Y | Y | Y | Y | Y | Y | Y
| Reference |  |  | RDHx_MaxHeat_Removal |  |  | Number | Constant Number | Power | PIT(2) | Extensive | Stand alone | [37 empty] | Y
| Reference |  |  | DTC_MaxCool_Capacity |  |  | Number | Constant Number | Power | PIT(2) | Extensive | Stand alone | [35 empty] | Y
| Metric |  |  | Capacity_Envelope | Capacity_Envelope = min(Power Capacity, Thermal Capacity) |  | Number | Constant Number | Power | PIT(2) | Extensive | Stand alone | [63 empty] | Y | Y | Y | Y | Y | Y | Y | Y
| Metric |  |  | Power_Capacity |  |  | Number | Constant Number | Power | PIT(2) | Extensive | Stand alone | [11 empty] | Y | Y | [50 empty] | Y | Y | Y | Y | Y | Y | Y | Y
| Metric |  |  | Thermal_Capacity |  |  | Number | Constant Number | Power | PIT(2) | Extensive | Stand alone | [11 empty] | Y | Y | [50 empty] | Y | Y | Y | Y | Y | Y | Y | Y
| Metric |  |  | Cell_Margin |  |  | Number | Constant Number | Power | PIT(2) | Extensive | Stand alone | [66 empty] | Y
| Metric |  |  | Cell_Margin% |  |  | Number | Constant Number | Ratio | PIT(2) | Intensive | Stand alone | [66 empty] | Y
| Metric |  |  | Cell_Utilization% |  |  | Number | Constant Number | Ratio | PIT(2) | Intensive | Stand alone | [66 empty] | Y
| Metric |  |  | Power_Margin |  |  | Number | Constant Number | Power | PIT(2) | Extensive | Stand alone | [63 empty] | Y | Y | Y | Y
| Metric |  |  | Power_Margin% |  |  | Number | Constant Number | Ratio | PIT(2) | Intensive | Stand alone | [63 empty] | Y | Y | Y | Y
| Metric |  |  | Thermal_Margin |  |  | Number | Constant Number | Power | PIT(2) | Extensive | Stand alone | [63 empty] | Y | Y | Y | Y
| Metric |  |  | Thermal_Margin% |  |  | Number | Constant Number | Ratio | PIT(2) | Intensive | Stand alone | [63 empty] | Y | Y | Y | Y
| Reference |  |  | Liquid_Cooling_Capacity | [41 empty] | Y
| Reference |  |  | Air_Cooling_Capacity | [41 empty] | Y
| Metric |  |  | Upstream_Capacity
| Metric |  |  | Upstream_Load
| Metric |  |  | Rack_Positions
Note on J32: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: can we using existed unit class "Percentage per Time"? Reply: yes
Note on J44: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Add new Unit Class Reply: Percent times Seconds, Percent times Minutes, Percent times hours
Note on J46: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Can we use Energy unit class? Reply: yes
Note on J85: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: use Angular Velocity as Unit class
Note on J105: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: We can use general dimensionless units for now Reply: Add new Unit Dimensionless under General Dimensionless Units

## Capacity Nodes
Node Type | Topology | Capacity Node (Capacity Domain) | ActiveConstraint
Rack PDU | Electrical System | FALSE | FALSE
RPP | Electrical System | TRUE | TRUE
Room PDU | Electrical System | TRUE | TRUE
UPS | Electrical System | TRUE | TRUE
BESS | Electrical System | TRUE | TRUE
Switch Gear | Electrical System | FALSE | FALSE
Utility Feed | Electrical System | TRUE | TRUE
Generator | Electrical System | TRUE | TRUE
RDHx | Cooling System | FALSE | FALSE
DTC | Cooling System | FALSE | FALSE
Air Zone | Cooling System | TRUE | TRUE
Liquid Lood | Cooling System | TRUE | TRUE
Air Cooling Unit | Cooling System | FALSE | FALSE
CDU | Cooling System | FALSE | FALSE
Cooling Distribution | Cooling System | TRUE | TRUE
Cooling Plant | Cooling System | TRUE | TRUE
Rack | Spatial Topology | TRUE | FALSE
Row | Spatial Topology | FALSE | FALSE
Zone | Spatial Topology | FALSE | FALSE
Aisle | Spatial Topology | FALSE | FALSE
Capacity Cell | Whitespace Blueprint | TRUE | FALSE | (passive constraint)
Room Bundle | Whitespace Blueprint | TRUE | FALSE | (passive constraint)
Room PDU Bundle | Whitespace Blueprint | TRUE | FALSE | (passive constraint)
UPS Bundle | Whitespace Blueprint | TRUE | FALSE | (passive constraint)

## Dependencies
Node Type | Dependency Node Type | Relationship Type | Topological Relationship | Upstream Level
Rack | RPP | Dependency | Upstream | 1
Rack | Room PDU | Dependency | Upstream | 2
Rack | UPS | Dependency | Upstream | 3
Rack | BESS | Dependency | Upstream | 4
Rack | Switch Gear | Dependency | Upstream | 5
Rack | Utility Feed | Dependency | Upstream | 6
Rack | Generator | Dependency | Upstream | 6
Rack | Air Zone | Dependency | Upstream | 1
Rack | Air Cooling Unit | Dependency | Upstream | 2
Rack | Liquid Loop | Dependency | Upstream | 1
Rack | CDU | Dependency | Upstream | 2
Rack | Cooling Distribution | Dependency | Upstream | 3
Rack | Cooling Plant | Dependency | Upstream | 4
Rack | RDHx | Dependency | Local
Rack | DTC | Dependency | Local
Row | RPP | Dependency | Upstream | 1
Row | Room PDU | Dependency | Upstream | 2
Row | UPS | Dependency | Upstream | 3
Row | BESS | Dependency | Upstream | 4
Row | Switch Gear | Dependency | Upstream | 5
Row | Utility Feed | Dependency | Upstream | 6
Row | Generator | Dependency | Upstream | 6
Row | Air Zone | Dependency | Upstream | 1
Row | Air Cooling Unit | Dependency | Upstream | 2
Row | Liquid Loop | Dependency | Upstream | 1
Row | CDU | Dependency | Upstream | 2
Row | Cooling Distribution | Dependency | Upstream | 3
Row | Cooling Plant | Dependency | Upstream | 4
Row | RDHx | Dependency | Local
Row | DTC | Dependency | Local
Zone | RPP | Dependency | Upstream | 1
Zone | Room PDU | Dependency | Upstream | 2
Zone | UPS | Dependency | Upstream | 3
Zone | BESS | Dependency | Upstream | 4
Zone | Switch Gear | Dependency | Upstream | 5
Zone | Utility Feed | Dependency | Upstream | 6
Zone | Generator | Dependency | Upstream | 6
Zone | Air Zone | Dependency | Upstream | 1
Zone | Air Cooling Unit | Dependency | Upstream | 2
Zone | Liquid Loop | Dependency | Upstream | 1
Zone | CDU | Dependency | Upstream | 2
Zone | Cooling Distribution | Dependency | Upstream | 3
Zone | Cooling Plant | Dependency | Upstream | 4
Zone | RDHx | Dependency | Local
Zone | DTC | Dependency | Local
Capacity Cell | RPP | Dependency | Local
Capacity Cell | Room PDU | Dependency | Upstream | 1
Capacity Cell | UPS | Dependency | Upstream | 2
Capacity Cell | BESS | Dependency | Upstream | 3
Capacity Cell | Switch Gear | Dependency | Upstream | 4
Capacity Cell | Utility Feed | Dependency | Upstream | 5
Capacity Cell | Generator | Dependency | Upstream | 5
Capacity Cell | Air Zone | Dependency | Local
Capacity Cell | Air Cooling Unit | Dependency | Upstream | 1
Capacity Cell | Liquid Loop | Dependency | Local
Capacity Cell | CDU | Dependency | Upstream | 1
Capacity Cell | Cooling Distribution | Dependency | Upstream | 2
Capacity Cell | Cooling Plant | Dependency | Upstream | 3
Capacity Cell | RDHx | Dependency | Local
Capacity Cell | DTC | Dependency | Local
Room Bundle | RPP | Dependency | Local
Room Bundle | Room PDU | Dependency | Upstream | 1
Room Bundle | UPS | Dependency | Upstream | 2
Room Bundle | BESS | Dependency | Upstream | 3
Room Bundle | Switch Gear | Dependency | Upstream | 4
Room Bundle | Utility Feed | Dependency | Upstream | 5
Room Bundle | Generator | Dependency | Upstream | 5
Room Bundle | Air Zone | Dependency | Local
Room Bundle | Air Cooling Unit | Dependency | Upstream | 1
Room Bundle | Liquid Loop | Dependency | Local
Room Bundle | CDU | Dependency | Upstream | 1
Room Bundle | Cooling Distribution | Dependency | Upstream | 2
Room Bundle | Cooling Plant | Dependency | Upstream | 3
Room Bundle | RDHx | Dependency | Local
Room Bundle | DTC | Dependency | Local
Room PDU Bundle | RPP | Dependency | Local
Room PDU Bundle | Room PDU | Dependency | Local
Room PDU Bundle | UPS | Dependency | Upstream | 1
Room PDU Bundle | BESS | Dependency | Upstream | 2
Room PDU Bundle | Switch Gear | Dependency | Upstream | 3
Room PDU Bundle | Utility Feed | Dependency | Upstream | 4
Room PDU Bundle | Generator | Dependency | Upstream | 4
Room PDU Bundle | Air Zone | Dependency | Local
Room PDU Bundle | Air Cooling Unit | Dependency | Upstream | 1
Room PDU Bundle | Liquid Loop | Dependency | Local
Room PDU Bundle | CDU | Dependency | Upstream | 1
Room PDU Bundle | Cooling Distribution | Dependency | Upstream | 2
Room PDU Bundle | Cooling Plant | Dependency | Upstream | 3
Room PDU Bundle | RDHx | Dependency | Local
Room PDU Bundle | DTC | Dependency | Local
UPS Bundle | RPP | Dependency | Local
UPS Bundle | Room PDU | Dependency | Local
UPS Bundle | UPS | Dependency | Local
UPS Bundle | BESS | Dependency | Upstream | 1
UPS Bundle | Switch Gear | Dependency | Upstream | 2
UPS Bundle | Utility Feed | Dependency | Upstream | 3
UPS Bundle | Generator | Dependency | Upstream | 3
UPS Bundle | Air Zone | Dependency | Local
UPS Bundle | Air Cooling Unit | Dependency | Upstream | 1
UPS Bundle | Liquid Loop | Dependency | Local
UPS Bundle | CDU | Dependency | Upstream | 1
UPS Bundle | Cooling Distribution | Dependency | Upstream | 2
UPS Bundle | Cooling Plant | Dependency | Upstream | 3
UPS Bundle | RDHx | Dependency | Local
UPS Bundle | DTC | Dependency | Local
Rack PDU | RPP | Dependency | Upstream | 1
Rack PDU | Room PDU | Dependency | Upstream | 2
Rack PDU | UPS | Dependency | Upstream | 3
Rack PDU | BESS | Dependency | Upstream | 4
Rack PDU | Switch Gear | Dependency | Upstream | 5
Rack PDU | Utility Feed | Dependency | Upstream | 6
Rack PDU | Generator | Dependency | Upstream | 6
RPP | Room PDU | Dependency | Upstream | 1
RPP | UPS | Dependency | Upstream | 2
RPP | BESS | Dependency | Upstream | 3
RPP | Switch Gear | Dependency | Upstream | 4
RPP | Utility Feed | Dependency | Upstream | 5
RPP | Generator | Dependency | Upstream | 5
Room PDU | UPS | Dependency | Upstream | 1
Room PDU | BESS | Dependency | Upstream | 2
Room PDU | Switch Gear | Dependency | Upstream | 3
Room PDU | Utility Feed | Dependency | Upstream | 4
Room PDU | Generator | Dependency | Upstream | 4
UPS | BESS | Dependency | Upstream | 1
UPS | Switch Gear | Dependency | Upstream | 2
UPS | Utility Feed | Dependency | Upstream | 3
UPS | Generator | Dependency | Upstream | 3
BESS | Switch Gear | Dependency | Upstream | 1
BESS | Utility Feed | Dependency | Upstream | 2
BESS | Generator | Dependency | Upstream | 2
RDHx | Liquid Loop | Dependency | Upstream | 1
RDHx | CDU | Dependency | Upstream | 2
RDHx | Cooling Distribution | Dependency | Upstream | 3
RDHx | Cooling Plant | Dependency | Upstream | 4
DTC | Liquid Loop | Dependency | Upstream | 1
DTC | CDU | Dependency | Upstream | 2
DTC | Cooling Distribution | Dependency | Upstream | 3
DTC | Cooling Plant | Dependency | Upstream | 4
CDU | Cooling Distribution | Dependency | Upstream | 1
CDU | Cooling Plant | Dependency | Upstream | 2
Air Zone | Air Cooling Unit | Dependency | Upstream | 1
Air Zone | Cooling Distribution | Dependency | Upstream | 2
Air Zone | Cooling Plant | Dependency | Upstream | 3
Air Cooling Unit | Cooling Distribution | Dependency | Upstream | 1
Air Cooling Unit | Cooling Plant | Dependency | Upstream | 2
Cooling Distribution | Cooling Plant | Dependency | Upstream | 1

## Impacts
Node Type | Impact Node Type | Topological Relationship | Downstream Level
Rack PDU | Rack | Load
RPP | Rack PDU | Downstream | 1
RPP | Rack | Load
RPP | Row | Load
RPP | Zone | Load
RPP | Capacity Cell | Load
RPP | Room Bundle | Load
RPP | Room PDU Bundle | Load
RPP | UPS Bundle | Load
Room PDU | Rack PDU | Downstream | 2
Room PDU | RPP | Downstream | 1
Room PDU | Rack | Load
Room PDU | Row | Load
Room PDU | Zone | Load
Room PDU | Capacity Cell | Load
Room PDU | Room Bundle | Load
Room PDU | Room PDU Bundle | Load
Room PDU | UPS Bundle | Load
UPS | Rack PDU | Downstream | 3
UPS | RPP | Downstream | 2
UPS | Room PDU | Downstream | 1
UPS | Rack | Load
UPS | Row | Load
UPS | Zone | Load
UPS | Capacity Cell | Load
UPS | Room Bundle | Load
UPS | Room PDU Bundle | Load
UPS | UPS Bundle | Load
BESS | Rack PDU | Downstream | 4
BESS | RPP | Downstream | 3
BESS | Room PDU | Downstream | 2
BESS | UPS | Downstream | 1
BESS | Rack | Load
BESS | Row | Load
BESS | Zone | Load
BESS | Capacity Cell | Load
BESS | Room Bundle | Load
BESS | Room PDU Bundle | Load
BESS | UPS Bundle | Load
Switch Gear | Rack PDU | Downstream
Switch Gear | RPP | Downstream
Switch Gear | Room PDU | Downstream
Switch Gear | UPS | Downstream
Switch Gear | BESS | Downstream
Utility Feed | Rack PDU | Downstream | 6
Utility Feed | RPP | Downstream | 5
Utility Feed | Room PDU | Downstream | 4
Utility Feed | UPS | Downstream | 3
Utility Feed | BESS | Downstream | 2
Utility Feed | Switch Gear | Downstream | 1
Utility Feed | Rack | Load
Utility Feed | Row | Load
Utility Feed | Zone | Load
Utility Feed | Capacity Cell | Load
Utility Feed | Room Bundle | Load
Utility Feed | Room PDU Bundle | Load
Utility Feed | UPS Bundle | Load
Generator | Rack PDU | Downstream | 6
Generator | RPP | Downstream | 5
Generator | Room PDU | Downstream | 4
Generator | UPS | Downstream | 3
Generator | BESS | Downstream | 2
Generator | Switch Gear | Downstream | 1
Generator | Rack | Load
Generator | Row | Load
Generator | Zone | Load
Generator | Capacity Cell | Load
Generator | Room Bundle | Load
Generator | Room PDU Bundle | Load
Generator | UPS Bundle | Load
Liquid Loop | RDHx | Downstream | 1
Liquid Loop | DTC | Downstream | 1
Liquid Loop | Rack | Load
Liquid Loop | Row | Load
Liquid Loop | Zone | Load
Liquid Loop | Capacity Cell | Load
Liquid Loop | Room Bundle | Load
Liquid Loop | Room PDU Bundle | Load
Liquid Loop | UPS Bundle | Load
CDU | RDHx | Downstream | 2
CDU | DTC | Downstream | 2
CDU | Liquid Loop | Downstream | 1
Air Zone | Rack | Load
Air Zone | Row | Load
Air Zone | Zone | Load
Air Zone | Capacity Cell | Load
Air Zone | Room Bundle | Load
Air Zone | Room PDU Bundle | Load
Air Zone | UPS Bundle | Load
Air Cooling Unit | Air Zone | Downstream | 1
Cooling Distribution | RDHx | Downstream | 3
Cooling Distribution | DTC | Downstream | 3
Cooling Distribution | Air Zone | Downstream | 2
Cooling Distribution | Liquid Loop | Downstream | 2
Cooling Distribution | CDU | Downstream | 1
Cooling Distribution | Air Cooling Unit | Downstream | 1
Cooling Distribution | Rack | Load
Cooling Distribution | Row | Load
Cooling Distribution | Zone | Load
Cooling Distribution | Capacity Cell | Load
Cooling Distribution | Room Bundle | Load
Cooling Distribution | Room PDU Bundle | Load
Cooling Distribution | UPS Bundle | Load
Cooling Plant | RDHx | Downstream | 4
Cooling Plant | DTC | Downstream | 4
Cooling Plant | Air Zone | Downstream | 3
Cooling Plant | Liquid Loop | Downstream | 3
Cooling Plant | CDU | Downstream | 2
Cooling Plant | Air Cooling Unit | Downstream | 2
Cooling Plant | Cooling Distribution | Downstream | 1
Cooling Plant | Rack | Load
Cooling Plant | Row | Load
Cooling Plant | Zone | Load
Cooling Plant | Capacity Cell | Load
Cooling Plant | Room Bundle | Load
Cooling Plant | Room PDU Bundle | Load
Cooling Plant | UPS Bundle | Load

## Taxonomy
M
Variable Taxonomy
Value Model |  |  | Evaluation Model
Time_Series |  |  | Realtime_PrePersist |  | metric updates immediately on arrival of realtime inputs (low latency), and does not require waiting for a persistence cycle to produce the updated value.
Event_Series | Discrete events with timestamp and payload |  | Realtime_PostPersist |  | metric updates only after the new inputs are persisted/committed (or after a persist-driven event), so it inherently waits for persistence.
Sanpshot | Static data that may only get updated from time to time |  | Batch_PostPersist |  | metric updates on batch schedule/trigger and reads persisted data.
State | State may gets updated upon new information |  | Batch_PrePersist |  | metrics computed during batch ingestion, before commit, using the in-flight batch and optional historical references, typically for validation, enrichment, or gating.
No_Evaluation
| Interna Name/ Variable Class | Examples | Value Model | Role | Evaluation Mode | Stream Processor | Batch Processor | Streaming Analytics Engine | Reporting Analytics Engine | Topology Consolidator
Metric-1 | Metric- Near Realtime Metric | Emisison Intensity, EA, Emissions | Time_Series | Computed | Realtime_PostPersist |  |  |  | RIT
Metric-2 (new) | Metric - Realtime Metric | Power Fitness Index | Time_Series | Computed | Realtime_PrePersist |  |  | RIT, RFQ
Metric-3 (new) | Metric - Reporting Metric | Power Overshoot at room or facility levels | Time_Series | Computed | Batch_PostPersist |  |  |  | RIT, RFQ
Object1 | Input- Batch Input (integreated, standalone) | BAR data, Fuel usage | Time_Series | Input | Batch_PrePersist |  | SIT |  |  | C-SIT
Object2 (new) | Input - Live Input (integrated, standalone) | Power_Usage, Operating_temperature | Time_Series | Input | Realtime_PrePersist | SIT |  |  |  | C-SIT
Field | Reference | Power_Limit | Snapsot | Input | No_Evaluation
Not yet used |  |  | Time_Series | Input | Realtime_PostPersist
Not yet used | Live State |  | State | Input | Realtime_PrePersist | SIT
Not yet used | Derived Live State |  | State | Computed | Realtime_PrePersist |  |  | RIT, RFQ
Not yet used | Persisted State |  | State | Computed | Realtime_PostPersist |  |  |  | RIT
Event
Functional Domains |  |  |  |  | RIT | The aggregation window used to compute one reported value.
| Power |  |  |  | RFQ | How often the metric emits or updates values. RFQ can also be on-persist or on-demand
| Electrical Energy |  |  |  | SIT
Thermal
Cooling
Utilization
Emission
Variable (Instance) Values
| Measured Value (M) |  | value acquired directly or indirectly through external input, not internal data topology consolidation
|  | Telemetry (M_T) | Value directly received from external systems, with no or minimum processing.
|  | Manual (M_M) | Value directly entered or uploaded by humans, with no or minimum processing
|  | Logical (M_L) | Value computed from other variables, but not calculated through topology consolidation
Derived Value (D)
Predicted Value (P)
Distributed Value (A)
Rollup Value (R)

## ContextScope
Context Group | Context | Path ID | Topology | Inclusion Type | Subgraph Definition | Lineage Anchor | Branch Root | Trim Node Type | Excluded Node Type | Blocked Edge Type | Data Topology (Consolidation Logic) | Node Types
Power usage | Power usage-Electrical | 1 | Electrical System | Topology | NA | NA | NA | NA |  |  | Smart Inclusive
Power usage | Power usage-RkGroup | 1 | Operational Infrastructure | Subgraph | Lineage | Rack | NA |  |  |  | Smart Inclusive
Rack rollup | Rack rollup-Spatial | 1 | Spatial Topology | Subgraph | Lineage | Rack |  |  |  |  | Standard Rollup
Rack rollup | Rack rollup-Whitespace | 1 | Whitespace Blueprint | Subgraph | Lineage | Rack |  | Containment Bundles |  |  | Standard Rollup
Rack rollup | Rack rollup-Placement Plan | 1 | Deployment Blueprint | Subgraph | Branch |  | Deployment |  |  | Cluster-Placement Draft | Standard Rollup
Rack rollup | Rack rollup-Placement Draft | 1 | Deployment Blueprint | Subgraph | Branch |  | Placement Draft |  |  |  | Standard Rollup
Rack rollup | Rack rollup-Electrical | 1 | Electrical System | Subgraph | Lineage | Rack |  | UPS |  |  | Standard Rollup
Rack rollup | Rack rollup-Air Cooling | 1 | Cooling System | Subgraph | Lineage | Rack |  |  |  | Liquid Loop-Rack | Standard Rollup
Rack rollup | Rack rollup-Liquid Cooling | 1 | Cooling System | Subgraph | Lineage | Rack |  |  |  | Air Zone-Rack | Standard Rollup

## VT
Variable Type | Variable Class | Functional Domain
Node_Fitness_Index | Metric | Composite
IT_OperatingMargin | Metric | Composite
TrueCost_Power | Metric | Composite
Batchability_PowerProxy_Factor | Metric | Compute
Batching_Fitness_Index | Metric | Compute
Batchability_PowerProxy_wt | Reference | Compute
Batching_Fitness_Index_wt | Reference | Compute
Fan_Speed | Input | Cooling
Liquid_ReturnT | Input | Cooling
Liquid_SupplyT | Input | Cooling
Pump_Control_Percent | Input | Cooling
Pump_Saturation | Input | Cooling
Pump_Speed | Input | Cooling
Cooling_Efficiency_Factor | Metric | Cooling
Cooling_Efficiency_Index | Metric | Cooling
Fan_Saturation | Metric | Cooling
Fan_Saturation_Factor | Metric | Cooling
Liquid_ReturndT_perkW | Metric | Cooling
Liquid_ReturndT_perkW_Factor | Metric | Cooling
Liquid_SupplyT_Margin | Metric | Cooling
Liquid_SupplyT_Margin_Factor | Metric | Cooling
LiquidCooling_Fitness_Index | Metric | Cooling
Pump_Saturation_Factor | Metric | Cooling
Cooling_Efficiency_wt | Reference | Cooling
Cooling_Efficiency_Index_wt | Reference | Cooling
Fan_Saturation_wt | Reference | Cooling
Fan_Speed_Limit | Reference | Cooling
Liquid_ReturndT_perkW_wt | Reference | Cooling
Liquid_SupplyT_Limit | Reference | Cooling
Liquid_SupplyT_Margin_wt | Reference | Cooling
LiquidCooling_Fitness_Index_wt | Reference | Cooling
Pump_Saturation_wt | Reference | Cooling
Pump_Speed_Limit | Reference | Cooling
Power_Overlimit_Event | Event | Power
Power_Usage | Input | Power
Breaker_Headroom | Metric | Power
Min_Headroom_UpstreamBreaker | Metric | Power
MinPower_Headroom_UpstreamBreaker | Metric | Power
Norm_Power_IncRate | Metric | Power
Norm_Power_Increase | Metric | Power
Power_Burstiness | Metric | Power
Power_Burstiness_Factor | Metric | Power
Power_Excess | Metric | Power
Power_Fitness_Index | Metric | Power
Power_Headroom | Metric | Power
Power_Headroom_Factor | Metric | Power
Power_JumpRating | Metric | Power
Power_Overlimit_Factor | Metric | Power
Power_Overlimit_Time | Metric | Power
Power_Overshoot | Metric | Power
Power_Peak_Probability | Metric | Power
Power_PeakRisk_Factor | Metric | Power
Power_RampRate | Metric | Power
Power_RampRate_Factor | Metric | Power
Power_SteepJump_Count | Metric | Power
Power_Usage_Std | Metric | Power
Relative_Power_Headroom | Metric | Power
Relative_Power_Overshoot | Metric | Power
Upstream_PowerRisk_Index | Metric | Power
UpstreamBreaker_Headroom_Factor | Metric | Power
Power_OperatingMargin | Metric | Power
Breaker_CurrentLimit | Reference | Power
Breaker_PowerLimit | Reference | Power
Effective_Power_Limit | Reference | Power
Power_Burstiness_wt | Reference | Power
Power_Derating_Factor | Reference | Power
Power_Fitness_Index_wt | Reference | Power
Power_Headroom_wt | Reference | Power
Power_Limit | Reference | Power
Power_Overlimit_wt | Reference | Power
Power_PeakRisk_wt | Reference | Power
Power_RampRate_wt | Reference | Power
Rated_Power_Capacity | Reference | Power
Upstream_PowerRisk_Index_wt | Reference | Power
UpstreamBreaker_Headroom_wt | Reference | Power
Thermal_Overheat_Event | Event | Thermal
Operating_Temp | Input | Thermal
Temperature | Input | Thermal
Local_Temp_Diff | Metric | Thermal
Temp_Overshoot | Metric | Thermal
Thermal_Coupling | Metric | Thermal
Thermal_Coupling_Factor | Metric | Thermal
Thermal_Excess | Metric | Thermal
Thermal_Fitness_Index | Metric | Thermal
Thermal_Headroom | Metric | Thermal
Thermal_Headroom_Factor | Metric | Thermal
Thermal_Hotspot_Factor | Metric | Thermal
Thermal_Overheat_Factor | Metric | Thermal
Thermal_Overheat_Time | Metric | Thermal
Thermal_OperatingMargin | Metric | Thermal
Thermal_Coupling_wt | Reference | Thermal
Thermal_Fitness_Index_wt | Reference | Thermal
Thermal_Headroom_wt | Reference | Thermal
Thermal_Hotspot_wt | Reference | Thermal
Thermal_Limit | Reference | Thermal
Thermal_Overheat_wt | Reference | Thermal

## NFI data (hidden)
Data Type | Node Type | Parameter Key | Uses Inputs | Display Name | short_label | Description | Unit | Variable Type
Metric (Telemetry) | GPU | raw.electrical_power.kW | [5 empty] | Power usage
Metric (Telemetry) | Server | raw.electrical_power.kW
Metric (Telemetry) | Rack _PDU_Outlet | raw.electrical_power.kW
Metric (Telemetry) | Rack | raw.electrical_power.kW
Metric (Telemetry) | Rack_PDU | raw.electrical_power.kW
Metric (Telemetry) | Rack | raw.inlet_temp.C
Metric (Telemetry) | Rack | raw.inlet_temp_top.C
Metric (Telemetry) | Rack | raw.inlet_temp_mid.C
Metric (Telemetry) | Rack | raw.inlet_temp_bottom.C
Metric (Telemetry) | Server | raw.Inlet_temp.C
Metric (Telemetry) | Server | raw.fanRPM
Metric (Telemetry) | Loop | raw.liquid_supplyTemp.C
Metric (Telemetry) | Loop | raw.liquid_returnTemp.C
Metric (Telemetry) | Loop | raw.electrical_power.kW
Metric (Telemetry) | Loop | raw.pump_speed_pct
Metric (Telemetry) | Loop | raw.pump_control_pct
Metric (Telemetry) | Utility_Meter | raw.electrical_power.kW
Metric (Telemetry) | Main_Switchgear | raw.electrical_power.kW
Metric (Telemetry) | Generator_Output | raw.electrical_power.kW
Metric (Telemetry) | ATS | raw.electrical_power.kW
Metric (Telemetry) | UPS_output | raw.electrical_power.kW
Metric (Telemetry) | Floor_PDU | raw.electrical_power.kW
Metric (Telemetry) | Branch_Circuit | raw.electrical_power.kW
Metadata (Static) | Rack_PDU | rated_capacity.kW
Metadata (Static) | Rack_PDU | breaker_limit.kW
Metadata (Static) | Rack_PDU | power_derating_factor
Metadata (Static) | Rack | effecitve_power_capacity.kW
Metadata (Static) | Rack | thermal_limit_inlet.C
Metadata (Static) | Rack | thermal_threshold_factor
Metadata (Static) | Server_PSU | psu_limit.kW
Metadata (Static) | Rack_PDU_Outlet | outlet_limit.kW
Metadata (Static) | Server_PSU | power_derating_factor
Metadata (Static) | Server_PSU | config_power_cap.kW
Metadata (Static) | Server | thermal_limit_inlet.C
Metadata (Static) | Server | max_fanRPM
Metadata (Static) | Loop | max_liquid_supplyTemp.C
Metadata (Static) | Utility_Meter | breaker_limit.kW
Metadata (Static) | Main_Switchgear | breaker_limit.kW
Metadata (Static) | Generator_Output | breaker_limit.kW
Metadata (Static) | ATS | breaker_limit.kW
Metadata (Static) | UPS_output | breaker_limit.kW
Metadata (Static) | Floor_PDU | breaker_limit.kW
Metadata (Static) | Branch_Circuit | breaker_limit.kW
Metadata (Static) | Rack | wt.power_headroom
Metadata (Static) | Rack | wt.power_rampRate
Metadata (Static) | Rack | wt.power_burstiness
Metadata (Static) | Rack | w.power_peakRisk
Metadata (Static) | Rack | wt.power_overlimit
Metadata (Static) | Rack | wt.thermal_headroom_10m
Metadata (Static) | Rack | wt.thermal_headroom_30m
Metadata (Static) | Rack | wt.thermal_coupling
Metadata (Static) | Rack | wt.local_hotspot
Metadata (Static) | Rack | wt.thermal_overheat
Metadata (Static) | Rack | wt.cooling_efficiency
Metadata (Static) | Server | wt.power_headroom
Metadata (Static) | Server | wt.power_peakRisk
Metadata (Static) | Server | wt.power_overlimit
Metadata (Static) | Server | wt.thermal_headroom_10m
Metadata (Static) | Server | wt.thermal_headroom_30m
Metadata (Static) | Server | wt.fan_saturation
Metadata (Static) | Loop | wt.liquid_supplyTemp_margin
Metadata (Static) | Loop | wt.liquid,dt_per_kW
Metadata (Static) | Loop | wt.pump_saturation
Metadata (Static) | Rack | wt.upstream_breaker_headroom
Metadata (Static) | Server | wt.batchability_proxy
Metadata (Static) | Rack | wt.power_fitness_rack
Metadata (Static) | Rack | wt.thermal_fitness_rack
Metadata (Static) | Rack | wt.cooling_efficiency_rack
Metadata (Static) | Server | wt.power_fitness_server
Metadata (Static) | Server | wt.thermal_fitness_server
Metadata (Static) | Loop | wt.liquid_cooling_fitness_loop
Metadata (Static) | Rack | wt.power_risk_upstream
Metadata (Static) | Server | wt.batching_fitness_server
Feature T1 | Rack | power_headroom.kW | Rack.raw.electrical_power.kW, Rack.effecitve_power_capacity.kW
Feature T2 | Rack | min.power_headroom.kW_30s | Rack.power_headroom.kW
Feature T2 | Rack | power_ramp_rate.kW_s | Rack.raw.electrical_power.kW
Feature T1 | Rack | power_incr_rate.kW_s | Rack.raw.electrical_power.kW | N
Feature T1 | Rack | power_jump_rating | Rack.raw.electrical_power.kW, Rack.effecitve_power_capacity.kW | N
Feature T2 | Rack | power_steepJump_freq | Rack.power_jump_rating | Y
Feature T2 | Rack | power_burstiness | Rack.power_incr_rate.kW_s, Rack.power_jump_rating
Feature T2 | Rack | power_peakRisk | Rack.raw.electrical_power.kW, Rack.effecitve_power_capacity.kW
Feature T1 | Rack | power_overLimit | Rack.raw.electrical_power.kW, Rack.effecitve_power_capacity.kW
Feature T2 | Rack | total_powerOvershoot | Rack.raw.electrical_power.kW, Rack.effecitve_power_capacity.kW
Feature T2 | Rack | power_overLimit_count | Rack.power_overLimit
Feature T2 | Rack | power_overLimit_freq | Rack.power_overLimit
Feature T2 | Rack | power_overLimit_time | Rack.power_overLimit
Feature T1 | Rack | thermal_headroom.C | Rack.raw.inlet_temp.C, Rack.thermal_limit_inlet.C
Feature T2 | Rack | min.thermal_headroom.C_10m | Rack.thermal_headroom.C
Feature T2 | Rack | min.thermal_headroom.C_30m | Rack.thermal_headroom.C
Feature T2 | Rack | thermal_coupling.C_kW | Rack.raw.electrical_power.kW, Rack.raw.inlet_temp.C
Feature T2 | Rack | hist_thermal_coupling.C_kW | Rack.raw.electrical_power.kW, Rack.raw.inlet_temp.C
Feature T1 | Rack | temp_diff.C | Rack.raw.inlet_temp_bottom.C, Rack.raw.inlet_temp_top.C
Feature T2 | Rack | max_temp_diff.C | Rack.temp_diff.C
Feature T1 | Rack | thermal_overheat | Rack.raw.inlet_temp.C, Rack.thermal_limit_inlet.C
Feature T2 | Rack | total_tempOvershoot | Rack.raw.inlet_temp.C, Rack.thermal_limit_inlet.C
Feature T2 | Rack | thermal_overHeat_count | Rack.thermal_overheat
Feature T2 | Rack | thermal_overHeat_freq | Rack.thermal_overheat
Feature T2 | Rack | thermal_overHeat_time | Rack.thermal_overheat
Feature T1 | Server | power_headroom.kW | Server.raw.electrical_power.kW, Server_PSU.psu_limit.kW
Feature T2 | Server | min.power_headroom.kW_30s | Server.power_headroom.kW
Feature T2 | Server | power_peakRisk | Server.raw.electrical_power.kW, Server_PSU.psu_limit.kW
Feature T1 | Server | power_overLimit | Server.raw.electrical_power.kW, Server_PSU.psu_limit.kW
Feature T2 | Server | total_powerOvershoot | Server.raw.electrical_power.kW, Server_PSU.psu_limit.kW
Feature T2 | Server | power_overLimit_count | Server.power_overLimit
Feature T2 | Server | power_overLimit_freq | Server.power_overLimit
Feature T2 | Server | power_overLimit_time | Server.power_overLimit
Feature T1 | Server | thermal_headroom.C | Server.raw.Inlet_temp.C, Server.thermal_limit_inlet.C
Feature T2 | Server | min.thermal_headroom.C_10m | Server.thermal_headroom.C
Feature T2 | Server | min.thermal_headroom.C_30m | Server.thermal_headroom.C
Feature T2 | Server | fan_saturation | Server.raw.fanRPM, Server.max_fanRPM
Feature T1 | Loop | liquid_supplyTemp_margin.C | Loop.raw.liquid_supplyTemp.C, Loop.max_liquid_supplyTemp.C
Feature T2 | Loop | min.liquid_supplyTemp_margin.C | Loop.liquid_supplyTemp_margin.C
Feature T2 | Loop | liquid.dT_per_kW | Loop.raw.liquid_supplyTemp.C, Loop.raw.liquid_returnTemp.C, Loop.raw.electrical_power.kW
Feature T2 | Loop | pump_saturation | Loop.raw.pump_speed_pct, Loop.raw.pump_control_pct
Feature T2 | Rack | upstream_breaker_headroom.kW | Utility_Meter.breaker_limit.kW, Main_Switchgear.breaker_limit.kW, Generator_Output.breaker_limit.kW, ATS.breaker_limit.kW, UPS_output.breaker_limit.kW, Floor_PDU.;breaker_limit.kW, Branch_circuit.breaker_limit.kW
Feature T2 | Server | batchability_proxy | Server.raw.electrical_power.kW
Normalized Feature | Rack | norm.power_headroom | Rack.min.power_headroom.kW_30s
Normalized Feature | Rack | norm.power_rampRate | Rack.power_ramp_rate.kW_s
Normalized Feature | Rack | norm.power_burstiness | Rack.power_burstiness
Normalized Feature | Rack | norm.power_peakRisk | Rack.power_peakRisk
Normalized Feature | Rack | norm.power_overlimit | Rack.total_powerOvershoot
Normalized Feature | Rack | norm.thermal_headroom_10m | Rack.min.thermal_headroom.C_10m
Normalized Feature | Rack | norm.thermal_headroom_30m | Rack.min.thermal_headroom.C_30m
Normalized Feature | Rack | norm.thermal_coupling | Rack.thermal_coupling.C_kW
Normalized Feature | Rack | norm.local_hotspot | Rack.max_temp_diff.C
Normalized Feature | Rack | norm.thermal_overheat | Rack.total_tempOvershoot
Normalized Feature | Rack | norm.cooling_efficiency | Rack.hist_thermal_coupling.C_kW
Normalized Feature | Server | norm.power_headroom | Server.power_headroom.kW
Normalized Feature | Server | norm.power_peakRisk | Server.power_peakRisk
Normalized Feature | Server | norm.power_overlimit | Server.total_powerOvershoot
Normalized Feature | Server | norm.thermal_headroom_10m | Server.min.thermal_headroom.C_10m
Normalized Feature | Server | norm.thermal_headroom_30m | Server.min.thermal_headroom.C_30m
Normalized Feature | Server | norm.fan_saturation | Server.fan_saturation
Normalized Feature | Loop | norm.liquid_supplyTemp_margin | Loop.min.liquid_supplyTemp_margin.C
Normalized Feature | Loop | norm.liquid,dt_per_kW | Loop.liquid.dT_per_kW
Normalized Feature | Loop | norm.pump_saturation | Loop.pump_saturation
Normalized Feature | Rack | norm.upstream_breaker_headroom | Rack.upstream_breaker_headroom.kW
Normalized Feature | Server | norm.batchability_proxy | Server.batchability_proxy
Dimentonal Index | Rack | idx.power_fitness_rack | Rack.norm.power_headroom, Rack.norm.power_rampRate, Rack.norm.power_burstiness, Rack.norm.power_peakRisk Rack.norm.power_overlimit
Dimentonal Index | Rack | idx.thermal_fitness_rack | Rack.norm.thermal_headroom_10m, Rack.norm.thermal_headroom_30m, Rack.norm.local_hotspot, Rack.norm.thermal_overheat
Dimentonal Index | Rack | idx.cooling_efficiency_rack | Rack.norm.thermal_coupling, Rack.norm.cooling_efficiency
Dimentonal Index | Server | idx.power_fitness_server | Server.norm.power_headroom, Sever.norm.power_peakRisk Server.norm.power_overlimit
Dimentonal Index | Server | idx.thermal_fitness_server | Server.norm.thermal_headroom_10m, Server.norm.thermal_headroom_30m, Server.norm.fan_saturation
Dimentonal Index | Loop | idx.liquid_cooling_fitness_loop | Loop.norm.liquid_supplyTemp_margin, Loop.norm.liquid,dt_per_kW, Loop.norm.pump_saturation
Dimentonal Index | Rack | idx.power_risk_upstream | Rack.norm.upstream_breaker_headroom
Dimentonal Index | Server | idx.batching_fitness_server | Server.norm.batchability_proxy
Node Fitness index | Compute Node | idx.fitness_computeNode | All dimensional Indexes